## Appendix-1
Appendix -1 Details of Facilities required at Service Building (Ground +1st floor+ Dining facility @ 2nd Floor model) with all architectural & asthetic finish:
Scope shall cover Design, prepration of detailed layout/ architectural drawings, GA drawings , Structural study report , Design Basis Report for approvals from TSPL . Scope shall cover the complete building with all interior /exterior civil/ structural works , Architectural works, carpentary,flooring, tiling, Aluminium type fasle ceiling, painting, sanitory facilities with Reed bed type STP, electrical wiring,cabling, Distribution panel, UPS, PA system , fire alarm/ fighting system with approvals from TAC, CCTV (IP based & LAN connected) , LAN network , connecting RCC road& drain , 2M wide paverblock pathway (200M) , PCC paved car shed , lawn development & etc .
S.No | Description of facilities | Size in M (Length X Breadth ) measured at inside wall & glass | QTY- TSPL | Area in SqM | Minimum facility details
1 | COO/CEO Office | 6X9 | 1 | 54 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting , 2 ceiling fans , Toughened glass partion + glass door in front side, 5 No UPS supply points & 3 No. LAN sockets at seat & meeting table, Al .Window with outside asthtic Al. grills & roller type curtails; Attached Toilet. ACP paneling at one side wall is to be done with power supply, LAN arrangement for fixing LED TV (shifting existing LED TV supply is envisaged)
| COO/CEO -TA Room (Attached to COO office) (with 5 visitor waiting facility) | 3X6 | 1 | 18 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, 1 ceiling fan , Toughened glass partion + glass door in front side, UPS supply points & 1 No. LAN sockets at seat
2 | Closed Cabin-Type | 4X3 | 12 | 144 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, 1 ceiling fan , Toughened glass partion + glass door in front side, Provision for digital LED TV connected to LAN network, 3 No. UPS supply points & 2 No. LAN sockets at seat , Al .Window with outside asthtic Al. grills & roller type curtails.
4 | Open Cubicle | 3X3 | 18 | 162 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, 1 ceiling fan per open cubicle, 1 ceiling fan per 4 work stations ,3 No UPS supply points per desk & 1 No. LAN sockets per desk , Room with Al .Window with outside asthtic Al. grills & roller type curtails
5 | Work stations | 2X2 | 65 | 260
6 | Toilet -1st Floor | 6X4 | 2 | 48 | Aluminium type false ceiling with IP55 LED down lights , 1 ceiling fan at wash basin, 1 exhaust fan per toilet & per urinal set , Room with Al .Window & Al. door, 1 Geaser per toilet, 4 Urinal sets per toilet, 3 EWC per toilet, 1 wash basin with granite desk& mirror + all other PHE accessories; Finishing shall be of high class level with superior material selection as per EIC directions
7 | Toilet -Ground Floor | 6X4 | 2 | 48
8 | Pantry- at Ground Floor | 3X6 | 1 | 18 | Normal painted roof ceiling, Al windows , wooden door, required LED tube lights, 1 Ceiling fan, 3 No. 16A MCB power points, SS kitchen Sink with other PHE accessories, platform with polished granite finish for 1M wide in L shape
9 | Pantry- at Ground Floor | 3X6 | 1 | 18 | Normal painted roof ceiling, Al windows , wooden door, required LED tube lights, 1 Ceiling fan, 3 No. 16A MCB power points, SS kitchen Sink with other PHE accessories, platform with polished granite finish for 1M wide in L shape
9 | Closed Dining Room at 2nd floor | 20X7 | 1 | 140 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, 1 ceiling fan per dining table, Room with Al .Window with outside asthtic Al. grills & roller type curtails, 3 No. 16A MCB metal clad power points
| Closed VIP Dining at 2nd Floor | 6X4 | 1 | 24 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, 1 ceiling fan per dining table, Room with Al .Window with outside asthtic Al. grills & roller type curtails, 3 No. 16A MCB metal clad power points
| Semi open type Dining at 2nd Floor | 6X16 | 1 | 96 | Steel structural works, Roof with highly asthetic Canvas fabric material, LED outdoor type lighting, ceiling fans
11 | Conference Room(50 sittings) with projector/videoconference | 6X12 | 1 | 72 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, required ceiling fans , Toughened glass partion + glass door in front side, Provision for digital LED TV connected to LAN network, 10 No UPS supply points & 10 No. LAN sockets at meeting table, Al .Window with outside asthtic Al. grills & roller type curtails; ACP paneling at one side wall is to be done with power supply, LAN arrangement for fixing LED TV (Supply of 42"LED TV is also envisaged)
| Conference Room (24 sittings) | 8X5 | 1 | 40 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, Toughened glass partion + glass door in front side, Provision for digital LED TV connected to LAN network, 4 No UPS supply points & 4 No. LAN sockets at meeting table, Al .Window with outside asthtic Al. grills & roller type curtails; ACP paneling at one side wall is to be done with power supply, LAN arrangement for fixing LED TV (Shiftinng of existing LED TV is envisaged)
12 | TP Room | 9X6 | 1 | 54 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting; Scope covers shifting of existing furniture, TP screens & other arrangements from existing TP room to new building TP room providing all required UPS supply & LAN connectivity ; ACP paneling with high asthetic interior decoration is required inside room .
13 | Meeting room (6 seated) attached with Reception | 4X3 | 2 | 24 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, Toughened glass partion + glass door in front side;
15 | Visitor- Reception with lounge & HE/SHE separate Toilets (8 sitting, 1 Receptionist table) | 4X6 | 1 | 24 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, ceiling fan -2 Nos, 3 UPS points, 1 LAN connection at Receptionist desk, Toughened glass partion & ACP panel works as per directions of TSPL EIC, Biometric punching access for door entry inside office
16 | Documentation & store Room with rail mounted Racks @ Annexure Building | 12 X7 | 1 | 84 | Normal ceiling painted+ LED lights+ fire detectors+ Fan
17 | IT /Server Room | 3X6 | 1 | 18 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, Biometric authorisation access
18 | Electrical Room | 3X6 | 1 | 18 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, Biometric authorisation access, required cable trench, false flooring , GI conduiting for distributing power supply , Fire retardant door, fire extinguisher, insulation mat , Exhaust fan
19 | Server UPS room with battery bank | 3X6 | 1 | 18 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, Biometric authorisation access,required cable trench, false flooring , GI conduiting for distributing power supply , Fire retardant door, fire extinguisher, insulation mat
21 | AHU Room ( For centralised AC) | 3X7 | 2 | 42 | Normal ceiling painted+ LED lights+ fire detectors+ Exhaust Fan
23 | Closed Room for Auditor (with 5 sittings) | 5X4 | 2 | 40 | Aluminium type false ceiling with under deck insulation + LED sky lights+ fire detectors+ centralised AC ducting, 1 ceiling fan , 5 No UPS supply points per desk & 5 No. LAN sockets at desk ;Toughened glass partion + glass door in front side;
26 | Walk way space inside building & stair case | 2.5MX 34M X2Floors | 1 | 170 | ACP panels, glas partitions, Windows with high asthetic looks as per TSPL EIC directions; RCC Staircase with Granite pathway+ SS hand rails, IP55 type LED fansy downlights
A | Total Built up Area in 2 storeyed (G+1) building+ 1Annexure building+1 Dining room at 2nd floor- Service building |  |  | 1600 | SqM
Other Facilities & Infrastructures
B | Other Required Facilities/ Infrastructure details Detailed BOQ in section -A9 | QTY | SqM
1 | M20 grade, 250mm thick PCC paved Car Parking with Shed Considered 500mm depth earth work, compaction, 150mm WBM, 250mm thick PCC | For 15 Nos | 300
2 | M20 grade, 250mm thick PCC paved Car Parking without Shed Considered 500mm depth earth work, compaction, 150mm WBM, 250mm thick PCC | For 20 Nos | 400
3 | STP for 120 personnel (reed bed natural STP system preferred) | 1
4 | Front Lawn , laNDSCAPING with decorative lightsing(150 SqM) | As per TSPL EIC directions | 150
5 | Connecting M30 grade RCC Road of 7M Wide & sideway RCC drains with 500mm depth earth work, compaction, 150mm WBM, 50mm PCC& 150mm RCC | 100 M | 700
Bid- Summary (Section wise)
Section | Description | Cost | UOM
A1 | Building structural |  | Lakhs INR
A2 | Building -Architectural |  | Lakhs INR
A3 | PHE- works |  | Lakhs INR
A4 | Lightning Protection |  | Lakhs INR
A5 | IT/ LAN |  | Lakhs INR
A6 | Lighting system |  | Lakhs INR
A7 | Electrical/ Centralised AC/ UPS/ Hydrant/ Fire alarm systems |  | Lakhs INR
A8 | Other Infra- Car parking/ STP/Landscape/ 100M Road |  | Lakhs INR
| Total Basic Cost |  | Lakhs INR
| Total Cost with GST |  | Lakhs INR
| Building Elevation details |  | UOM
| FL | 0.45 | M
| Roof | 3.65 | M
| Roof 1st | 6.85 | M
| Parapet wall height | 1.1 | M
| Canteen @2nd floor | 10.05 | M

## Structural
Schedule-A1
STRUCTURAL WORKS - Servcie Building
Sl. No. | Particulars | Unit | Qty | Rate | Amount
1 | EXCAVATION
1.01 | Excavation in all types of soil including dense soil, disintegrated/ weathered/ soft rock (Poclainable) for Footings of columns, Retaining walls, Core walls, catch pits, Lift pits, trenches for drains, etc., by mechanical means including manual excavation for leveling, dressing the edges, with all leads and lifts including back filling in layers of 150mm with watering and compaction. Dewatering of both ground and surface water, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, struting, required for keeping earth in position etc, Rate to include disposing the excess earth and spreading in layers to the required levels within the site wherever specified and carting away out side the site to the designated areas identified by the local authorities. Note:PCC area shall be considered for measurement (Working space & provision of slopes if required for execution shall not be paid separately). | Cum | 500
1.02 | Supply and filling in foundations and the area whereever specified with approved good quality filling materials in plinths, area development etc. wherever specified in layers of not exceeding 150 mm thick including breaking clods,storing,transportation ,double handling, watering, compacting each layer with vibratory compactor and at unaccessible places with wooden/steel rammers to achieve 90 to 95% proctor density at optimum moisture content, all leads and lifts, bailing/ pumping out of water to keep site dry while backfilling; cost shall include conveyance of all materials, labour, machinery etc. complete as directed.The rate to includes loading,unloading, hire and fuel charges for tools and plants and other incidental charges etc., complete.
a | With excavated earth available at site ( for Foundtion & Sides of Retaining walls) | Cum | 400
b | With approved quality earth brought from outside | Cum
1.03 | Supplying and filling in plinth /under floors with Ghaggar sand including, watering, ramming consolidating and dressing complete | CuM | 135
Sub total for Earthwork
2 | CONCRETE
2.01 | Providing and laying P.C.C. 1:4:8 of specified th. wherever specified using river sand, 40mm and down size metal including sub grade preparation,leveling, all leads and lifts,rough finishing at the top surface,curing and shuttering if necessary etc., | Cum | 150
2.02 | READY MIX CONCRETE / CONTROLLED CONCRETE
NOTE: PARTY IS ALLOWED TO SET UP THEIR OWN READY MIX CONCRETE BATCHING PLANT AT SITE OR ALLOWED TO PROCURE FROM RMC PLANT THE PROBABLE CONCRETE FROM OUTSIDE WITH ALL QUALITY CONTROL MEASURES
Providing, batching, mixing, transporting through transit mixers, pumping and laying Reinforced Cement Concrete of specified grade at all levels and heights specified below using ordinary Portland cement of grade 53 from approved manufacturer, river sand, 20mm and down size coarse aggregates, necessary admixtures approved by Consultants (Conplast SP 430SRV from Fosroc or equivalent), including all leads and lifts, pumping using line pump or boom placer, vibrating/ compaction, scaffolding wherever necessary, curing as directed, including cost of shuttering and centering etc.
(Design mix shall be as approved by the Structural Consultant / Employers representative. Micro silica to be used for the Concrete of higher grde than M45 Grade )
M25 Grade
2.021 | Columns
| Ground floor | Cum | 60
| First floor | Cum | 40
2.022 | Slab
| First Floor | Cum | 150
| Terrace Floor | Cum | 150
2.023 | Beams
| First Floor | Cum | 70
| Terrace Floor | Cum | 70
2.025 | Staircase at all floors & heights | Cum | 8
2.026 | Plinth Beams | Cum | 35
2.027 | Isolated/ combined Footing | Cum | 200
Sub Total Concrete
3 | STEEL
3.01 | Supply, Fabricating & fixing in position reinforcement for RCC work with high yield strength ribbed cold twisted tor steel (HSD) bar of various diameters and grade of steel as specified below conforming to IS specification including cutting, providing, supplying & bending, hoisting, fabricating and placing in position according to drawings and binding the reinforcement with galvanised annealed binding wire of double fold of 18 gauge and providing PVC cover blocks for placing the reinforcements in position and for maintaining the cover specified and/or according to relevant IS.
Note : Unless noted otherwise the measurements in accordance with IS 1200. However reinforcement shall be measured only in lengths of bars as actually placed in position on standard weight basis, no allowance being made in the weight for rolling margin. Authorised laps and splices only will be measured. Chairs of any shape & profile, Spacer bar of any shape & profile, cover block, wastage and binding wire will not be measured and shall be included in the quoted rates.Quoted rate shall be deemed to have considered the above stipulation.Quoted rate to include lead, lift, placing at all levels and as directed.
| Fe 415 | MT | 100
3.02 | Supply, fabrication, erection, painting with 2 coat zinc rich primer & 2 coat epoxy paint of MS Steel structural jobs as per detailed engineering & directions of EIC (All ISA, ISMB,ISMC etc materials covered) | MT | 10
Sub Total Steel
4 | WATERPROOFING WORKS
4.01 | TERRACES
Providing waterproofing to the roof by the following method with min. 10 years guarantee.
| Providing and laying integrated cement based chemical water proofing treatment over R.C.C. roof slab / chajjas by cleaning the surface and spreading cement slurry over the surface. The base layer shall be chemical treatment which creates proper bonding through crystalline/ equivalent methodology. And laying average 100mm thick broken first class quality bricks in CM 1:5 and mixed with water proofing compound to required gradients and top finished with leakproof jointless waterproof plaster, 25mm thick, finished smooth with wooden trowel with false squares of 300x 300mm & with rounding off the joints between slab and wall with necessary curing etc., complete along with manufacturers guarantee of 15 years. | Sqm | 680
Total Cost

## Architectural
Schedule-A2
ARCHITECTURAL WORKS- Service Building
S.no | Item no | Description | Unit | Quantity | Rate | Amount
1 | MAS | MASONRY WORKS
1.01 | MASFA 01 | Providing and constructing Fly ash / burnt clay brick masonry, 230mm thick wall using table moulded bricks with minimum crushing strength of 50kgs /Sq cm (of A Grade) in CM 1:4 (1 cement: 4 coarse sand) and soaked 24 hours in water before using for construction with necessary scaffolding, staging, striking and raking out joints at least 10mm depth, at all lead and lift at all levels, curing, cost of labour, materials, loading and unloading, transportation and all other incidental charges etc., complete and as directed by the Engineer-in-charge. | Cum | 48.691
1.02 | MASFA 02 | Providing and constructing Fly ash/ burnt clay brick masonry, 115 mm thick wall using table moulded bricks with minimum crushing strength of 50kgs /Sq cm (of A Grade) in CM 1:4 (1 cement: 4 coarse sand) and soaked 24 hours in water before using for construction with necessary scaffolding, staging, striking and raking out joints at least 10mm depth, at all lead and lift at all levels, curing, cost of labour, materials, loading and unloading, transportation and all other incidental charges etc., complete and as directed by the Engineer-in-charge. | CuM | 40
1.03 | MASAAC 03 | Brick work with Autoclave Aerated Concrete (AAC) Blocks in superstructure above plinth level in all shapes and sizes in: Cement mortar 1:4 (1 cement : 4 coarse sand) from G.F plinth LVL with all accessories like bonding chemicals etc. | CuM | 214.912
TOTAL FOR MASONRY WORKS
2.00 | FLO | FLOORING WORKS
Note : Wastages will not be paid extra.Flooring to be covered with POP before handing over.
2.01 | FLO 01 | Providing and laying Cement Screed Concrete (Smooth finish) of 50mm thick average in cement concrete 1:2:4 using 12mm and down graded aggregates to be finished to receive the flooring, includes compacting, curing, grooving of joints, etc, complete and with all leads and lifts, and as per the instructions of Engineer in Charge. | Sqm | 1000
2.02 | FLO 02 | Providing and laying 1st quality ceramic glazed floor tiles ( Kajaria/Johnson/ NITCO or equivalent Digital series ) (including treads) or as per Engineer-in- Charge over 20mm thick cement mortar 1:4 mix, jointing with grey cement slurry including pointing with white cement mixed with pigment of matching shade including cost of all materials, labour etc. | Sqm | 144
2.03 | SKR 02 | Providing and laying 1st quality ceramic glazed wall tiles ( Kajaria/ johnson Digital series NITCO/ or equivalent ) or as approved by the Engineer-in-Charge in skirting, dado, risers, etc. over 12mm thk. cement mortar 1:3 mix, jointing with grey cement slurry including pointing with white cement mixed with pigment of matching shade including cost of all materials, labour etc., | SqM | 300
2.04 | FLO 03 | Providing and laying Vitrified tile flooring of Nitco/Kajaria/Johnson or any other approved make, size 600 X 600 mm, finished with paper thin joint and to required slope, set on 20mm thick cement mortar 1:4, grouting of joints with matching colour pigments / cement,curing, protecting the tiles by covering with POP/ Jute for the same. The cost shall include providing patterns, borders, inlays etc complete with all leads & lifts at all levels and heights including all wastages etc as per specifications and drawings, and as per the instructions of Engineer in Charge. Oxalic acid washing to be done on the tiled areas before handing over.(Basic rate Rs.50/Sft) | Sqm | 1510
2.05 | SKR 02 | Providing and laying 100mm height Vitrified tile Skirting of Nitco/Kajaria/Johnson or any other approved make of size 600 X 600 mm . The rate shall include the cost of epoxy grouting of joints to match the colour of tiles, chasing of wall to flush the skirting in line with the wall, fixing with approved adhesives , oxalic acid washing etc complete, with all leads & lifts at all levels and heights as per specifications given in the drawings, and as per the instructions of Engineer in Charge. Wastages shall not be paid extra.(Basic rate Rs.50/Sft) | Rmt | 540
2.06 | FLO 04 | Providing and laying single piece machine cut 20mm thk Pre polished Granite stone slab flooring (Staircase & other areas ) to be layed over a bed of 20-25mm thick CM 1:4 inclusive of grouting of joints with pigment to match the colour of stone,curing, covering with P.O.P/ jute & cleaning when required. The rate shall include wastages, providing patterns, borders, nosing,inlays etc complete with all leads & lifts at all levels as per specifications given in the drawings, and as per the instructions of Engineer in Charge.The rate shall include removal of POP, buffing and final cleaning etc complete. (Basic price :90/Sft) | Sqm | 150
2.07 | SKR 04 | Providing and laying 10mm thk Pre-polished granite tile skirting, 100mm high, to match with flooring, (Staircase)fixed with adhesives flushed to wall , including chasing walls wherever necessary, making good the chased surface, finished with paper thin joint, grouting, cleaning, pointing of joints with white/coloured cement. The rate shall include wastages, leads & lifts at all levels as per specifications given in the drawings, and as per the instructions of Engineer in Charge. (Basic price :90/Sft) | Rmt | 70
2.08 | FLO 06 | Providing and fixing Vinyl flooring of approved make and colour. The flooring shall be of 2mm thickness, homogenous, monolithic & fully flexible with approved width and length. The flooring shall be stuck properly with approved adhesive on the floor and shall be free of air bubbles. The floor base should be levelled in order to acheive smooth base. The joints shall be properly matched to provide seamless joints etc., complete (with all leads & lifts at all levels) as per Manufacturers specifications and as directed by Engineer Incharge. (Basic price of vinyl :60/sft) | Sqm | 20
2.09 | FLO 08 | Providing and laying Terracotta tile flooring of 1'x1' or 2'x2' size as approved by the architects , of approved colour and design over a bed of waterproof cement mortar 1:4 on porticos etc., laid to required pattern with spacer, slope to drain water to the outlets including grouting the joints with matching colour pigmented cement slurry, removing the excess slurry after grouting, cleaning the surface, curing for required period etc., complete. The rate shall include providing patterns, borders, inlays etc complete with all leads & lifts at all levels as per specifications given in the drawings, and cleaning the tiles suitably and hand over the same in a good condition as per the instructions of Engineer in Charge. (Basic rate Rs.40/Sft ) | Sqm | Ro
2.10 | SKR 08 | Providing and laying 100mm height Terracota tile (Terrace) Skirting of approved colour cut to size, neat machine cut , with paper thin joint , set in 20mm thick cement mortar 1:4, pointing of joints to match the colour of tiles, chasing of wall, finishing with CM 1:4,curing, etc., complete. With all leads & lifts at all levels and as per the instructions of the Engineer-in-charge. The rate shall be inclusive of cleaning the tiles suitably as instructed and hand over in a good condition as per the instruction of the Engineer in Charge (Basic rate Rs.40/Sft ) | Rmt | Ro
TOTAL FOR FLOORING WORKS
3.00 | CLD | DADO / CLADDING WORKS
3.01 | CLD 01 | Providing and Laying to pattern, Ceramic tile dado of Nitco/Kajaria/Johnson (or other equivalent approved make)of size 300 X450 mm or the size approved by the architects with required shade and colour as approved, laid to the pattern over 6-10mm thick tile adhesive ( M/s BAL/ M Y K Laticrete adhesive or approved equivalent), corners to have PVC edge beading. Work to include pointing with the matching colour grout, acid washing, necessary spacers to ensure uniform joints etc. complete.The rate shall include for borders, pencil borders etc., at all levels as per specifications including all leads and lifts, and as per the instructions of Engineer in Charge, (Basic rate Rs.40/Sft) | Sqm | 220
3.02 | CLD 02 | Providing and laying in position to pattern called for Brick cladding to walls /columns and other vertical faces laid over backing of 20mm thick cement mortar 1:4 laid over cement slurry, joints filled and finished neat with pigmented white cement including necessary grooves, curing etc., complete at all levels as per specifications and drawings. The rate shall includes all scaffolding, curing, all incidental charges etc., complete with all leads & lifts, at all levels as per the instructins of the Engineer in charge | Sqm | Ro
3.03 | CLD 03 | Providing & laying Dry Brick cladding of Wienerberger (Argeton) for external walls of the building, of approved size and colour of and quality with Aluminium substructure with horizontal support rails , with Aluminium joint and edge profiles (joint profile for water draining with ACP structure at the bottom) with necessary clips,fixtures all as per the manufacturers specifications. (Wastages shall not be paid extra) | Sqm | Ro
TOTAL FOR CLADDING WORKS
4.00 | PLA | PLASTERING WORKS
4.01 | PLA 01 | Preparing the surface, providing & applying plastering to Internal Ceiling ,soffits of staircase/beams surfaces etc of 10 mm thick with lime rendering in CM 1:4 (1 cement: 4 fine sand) at all levels including hacking, scraping, cleaning the surface, rounding of corners wherever required/specified, curing and includes cost of materials, labour, all leads and lifts at all levels, loading and unloading , transportation, with necessary scaffolding and all other incidental charges etc. complete and as directed by the Engineer-in-charge. | Sqm | 1748
4.02 | PLA 02 | Preparing the surface, Providing & applying plastering to Internal masonry walls, columns, beams, jambs etc., 12mm thick with lime rendering in CM 1:6 (1 cement: 6 fine sand) with lime rendering in line and at all levels including hacking to RCC surfaces, fixing of Corner beads for corner protection, & providing 150 mm wide GI plaster mesh Arpitha or equivalent approved make in the junctions of the masonry & RCC works, over electrical conduiting and wherever applicable as per manufacturer's specifications, plastering the mesh in CM 1:2. The work shall include cost of materials, labour, curing, all lead and lifts at all levels, loading and unloading, transportation, scaffolding and all other incidental charges etc., complete and as directed by the Engineer-in-charge. | Sqm | 1600 |  |  | 1032
4.03 | PLA 03 | Preparing the surface, providing & applying Sponge finish Plastering for external walls in two layers of base coat with 12mm thick in CM 1:6 & finishing coat 8mm thick in CM 1:4 laid in panels with jointless finish as per design including cement punning of cornices/projection/grooves, scaffolding, drip mould of all shape and sizes, fixing of Corner beads for corner protection, & 150 mm wide GI plaster mesh Arpitha or equivalent approved make in the junctions of the masonry & R.C.C work, over electrical conduiting, & wherever applicable as per manufacturer's specifications and plastering the mesh in CM 1:2. The work shall include cost of materials, labour, curing, all lead and lifts at all levels, loading and unloading, transportation, scaffolding and all other incidental charges etc. and also provision for groove cutting wherever required, complete and as directed by the Engineer-in-charge. The rate to include providing grooves of 15-20mm wide if any, wherever required as per the drawings. | Sqm | 1600
4.04 | PLA 04 | Preparing surface, providing and applying Rough plaster for wall (to receive tiling work for Granite/ Marble/ ceramic/ vitrified tiles) with 10mm thick cement mortar 1:6. The work shall include cost of materials, labour, loading and unloading, transportation, curing, scaffolding and all other incidental charges, with all leads & lifts at all levels.etc., complete and as directed by Engineer-in-charge. | Sqm | 220
4.05 | PLA 05 | Preparing the surface, Providing & applying Plastering to masonry wall, RCC surfaces, 15mm thick in single coat to Service shafts, ducts, etc., in CM 1:6 (1 cement: 6 fine sand) with waterproof compound (conplast or equivalent of approved make) & sand faced (Sponge) finish at all levels, curing, proper hacking to RCC surfaces, including fixing of 150mm wide GI plaster mesh Ariptha or equivalent of approved make in the junctions of the masonry & RCC work wherever applicable as per manufacturer's specifications, plastering the mesh in CM 1:2. The work shall include cost of materials, providing grooves as per design, labour, curing, all lead and lifts at all levels, loading and unloading, transportation, scaffolding and all other incidental charges etc., complete and as directed by the Engineer-in-charge. | Sqm | 200
TOTAL FOR PLASTER WORKS
5.00 | PAI | PAINTING WORKS
5.01 | PAI 01 | Providing and applying Acrylic emulsion paint finish -2 coat of Birla putty+1 coat of w/b primer + 3 coats of emulsion paint of asian/berger/jotun make for Ceilings of approved colour, preparing the surface by cleaning/sanding, filling up the cracks with crack filler, erecting and dismantling of scaffolding as & when it is required, finishing the surface with roller etc., complete. Note: Contractor shall arrange for his own scaffolding materials, ladders etc., legs of the ladders shall be covered properly with gunny bags so that floor does not get damaged. Floor shall be properly covered with plastic sheets to avoid spillage of paint while applying etc., with all leads & lifts at all levels complete and as directed by Engineer-in-charge. | Sqm | 1748
5.02 | PAI 02 | Providing and applying Acrylic emulsion paint for interiors walls with 2 coats of Birla white wall putty +1 coat of w/b primer and two coats of emulsion paint of asian/berger/jotun make, for walls of approved colour. And preparing the surface by cleaning/sanding, filling up the cracks with crack filler, erecting and dismantling of scaffolding as & when it is required, finishing the surface with roller etc., complete. Note: Contractor shall arrange for his own scaffolding materials, ladders etc., legs of the ladders shall be covered properly with gunny bags so that floor does not get damaged. Floor shall be properly covered with plastic sheets to avoid spillage of paint while applying etc., complete with all leads & lifts at all levels complete and as directed by Engineer-in-charge. | Sqm | 1600
5.03 | PAI 05 | Providing and applying Apex Weather proof emulsion (Heavy Textured Paint finish) for external walls with asian (or berger, jotun make) of Duracast fine tex of approved shade and colour for external walls including preparing the surface by cleaning/sanding, filling up the cracks with crack filler,3 coats of paint, erecting and dismantling of scaffolding, finishing the surface etc.,with all lead and lifts at all levels etc complete, as per the instructions of Engineer-in-charge. | Sqm | 1500
5.04 | PAI 06 | Providing and applying 2 coats of Oil bound Distemper of approved shade /colour/make over a coat of primer.the rate to include preparing the surface ,scaffolding etc complete at all leads and lifts as per the instructions of the Engineer in charge. | Sqm | Ro
5.05 | PAI 07 | Providing and applying 2 coats of White wash (manufactured by SURFACOATS)/SNOWCEM, of approved color/shade, over one coat of JK/BIRLA white cement primer over sponge plastered surface (inside ducts) etc., including preparing the surface by cleaning the cement mortar, removing the dust/dirt/oil/grease, sanding, filling up the dents, cracks, undulations with crack filler of approved make, erecting and dismantling of scaffolding, curing etc., complete with all leads & lifts at all levels complete and as directed by Engineer-in-charge. | Sqm | 20
TOTAL FOR PAINTING WORKS
6.00 | FAB | NON-STRUCTURAL METAL WORKS
Note: The rate to include necessary anchoring,baseplates,nuts,bolts etc for boxing,grouting if any wherever required even if not specified in the individual specification.
6.01 | FAB 01 | Providing ,Fabricating and fixing in position Powder coated MS railings (Ext staircase)using Tata Tube or equivalent make of ,1.1m ht with MS top rail of 50mm dia and 3 rows of 25mm dia bottom horizontal rails of MS tubular sections with required vertical supports of MS 20mm flats as specified in detailed drawings or at a span of 1.2m to 1.5m c/c as per site conditions .All MS sections to be treated with two coats of enamel painting over a coat of primer and the work to include the cost of materials,labour,machinery all leads and lifts complete as directed by the Engineer -in-charge | Kgs | 1300
6.02 | FAB 02 | Providing, fabricating and fixing in position Stainless steel railings of approved make as per design, detailed drawing and specifications, fixing as per standards ( SS grade 304: 18SWG) of 1mt ht with SS tube handrail of 50mm dia supported by verticals of 10mm SS Flat as per the span & conditions of the site or at a span of 1.2-1.5m as per site condition , with glass of 10mm thickness fixed to the railing suitably with all accessories as specified by EIC including, fixing with SS clamps, lugs, plates with all necessary fixtures etc., with all leads and lifts at all levels etc., complete and as directed by the Engineer- in-charge.Rate to include covering the railing structure with protective sheet before handing over. | Rmt | 50 |  |  | 25
6.03 | FAB 03 | Providing, fabricating and fixing in position Stainless steel railings (Internal Staircase) of approved make as per design, detailed drawing and specifications, fixing as per standards ( SS grade 304: 18SWG) of 1mt ht with SS tube /horizantals/ verticals & balusters. The top rail is of 50mm dia and with verticals of 30x30mm Box section at intervals as specified in the drawing or at 1.2-1.5m as per site condition , supported with 4 rows of horizontal railings of 25mm dia stainless steel tubes of required gauge as specified in detailed drawings, with suitable anchoring arrangements to walls and steps, necessary welding, base plates, screws, clamps and necessary hardwares, lugs etc complete. at all leads and lifts. The joints to be approved by the engineer in charge.The rate also to include necessary buffing, covering the railing with proper protective covers before handing over etc complete. | Rmt | RO
6.04 | FAB 04 | Providing ,Fabricating and fixing in position Powder coated MS Railing (Terrace) using Tata Tube or equivalent make of , with MS top rail of 50mm dia with required vertical supports as specified in detailed drawings or at a span of 1.2m as per the site conditions .All MS sections to be treated with two coats of enamel painting over a coat of primer and the work to include the cost of materials,labour,machinery all leads and lifts complete as directed by the Engineer -in-charge | Kgs | 700
TOTAL FOR NON STRUCTURAL METAL WORKS
7.00 | WWK | WOODEN/ FIRE DOORS AND JOINERY WORKS
Glass to be of Saint Gobain make even if not specified in the specification. All doors and windows to be provided with locks of Godrej/Magnum/Dorset make,sealants ,hinges,handles and door stoppers even if not specified.
7.01 | WWK01 | Providing and fixing well seasoned first quality Sal wood doors of width as per EIC directions, with the rebated frames of 125mmx62.5mm ( 5"x2.5" ) size to be fixed on to the walls using MS hold fasts 3 Nos ( Flat iron of 400x25x6mm ) on either side embedded in concrete 1:2:4. The frames shall be painted 2 coats of enamel paint ,make & shade as approved by the Architects over a coat of primer at all the lvls and heights. Supply & fixing of Single Flush shutter 35 mm thk of greenply/archidply fixed to frame with hinges and shutter finished with 1.5mm laminate both sides and vision panel of size in glass of 5mm thk fitted into EPDM gasket and of SaintGobain/Modi/Asahi make all as per design details. The rate shall include for providing and fixing of PVC/wooden beading all around at the masonry and frame junction if required , necessary hardwares- Godrej/Magnum/Dorset make,SS- hardware and hinges, handle ,towerbolts ,sealants etc complete with all the required accesories and as per the instructions of Engineer in Charge. (Location :Internal Doors- Doc rooms, Pantry) | Sqm | 15
7.02 | WWK01A | Item same as above (WWK01) but without vision panel all as per details in the drawings. | Sqm | Ro
7.03 | WWK05 | Providing and Fixing of 2 hour Fire rated Door with well seasoned Hardwood door with width of door as per IS3614 and frame section of 145mmx70mm with heat activated intumescent fire seal strip of section 10x4mm and one coat of antitermite fire retardant primer of make and shade as approved by the Architects. Supply and fixing of 55mm thk Asbestos free Composite Fire/Smoke check wooden double shutters with veneer on both sides and Vision Panel of Wired Glass 4-5mm thk on one of the shutters and 120 min Fire resistant rating confirming to BS :476 part -22 & IS :3614 Part -II comprising of two 9mm thk Starpan calcium silicate boards 100% without Asbestos,Brucite and Meerschaum having density not less than 1150kg/m3 and thermal conductive 0.14W sandwiching 31mm thk fire resistance insulation filler coated with FR silicon sealant and faced with 3mm thk Commercial ply on both sides with heal activated intumescent fire seal strip of size 10mmx4mm mounted in the grooves of hardwood lipping on all sides except bottom.The intemescent sealant is used to fill the gaps between board and internal wooden lipping. The rate to include all Hardwares /Fittings of approved make with all leads and lifts etc complete. (LOCATION: 2 No. emergency Exit Door, Electriical, UPS room, 2 AHU rooms,Store room) | Sqm | 32
TOTAL FOR DOORS AND JOINERY WORKS
8.00 | ADW | TOUGHENED GLASS WORKS & ALUMINIUM WORKS
Note : All windows to have a proper Drain sections .Kindly refer the all details and to provide silicone sealants/Gaskets wherever required.All surface to be done smooth ,wastages shall not be paid extra.Rate to include all accessories including screws,locking arrangement as per standard if any . Glass to be of Saint Gobain make even if not specified.
8.01 | ADW 01 | Providing and fixing in position SS Patch fitted Glass door and Glass- side panels & over panels ,using 12 mm thick Toughened Glass, door shutter mounted on SS corner patch fitting brushed steel finish, with floor springs of Everite or approved make, corner locks, SS handles and finishing the same complete and as directed by Engineer-in-charge. (Includes all leads and lifts at all levels); Transparent / opaque design on glass with asthetic look to be achieved by way of acid etching/ 3mm stickering as per directions of EIC Location- Front partion & door of all cubicles, conference / meeting rooms | Sqm | 390
8.02 | ADW 02 | Design, Supply, Fabrication and Fixing Aluminium Sliding Window , Powder coated to minimum 60 microns thickness (as per IS 7088) of Hindalco/Jindal or(or equivalent make) with two track sliding shutter in 5mm thick Clear Plain Glass of Saint Gobain make using for intermediate hooks duly fitted with standard accessories, fittings and EPDM siliconised gasket complete as per design, details and specification and approved by the EIC architect, including all hardware and consumables, sealing of joints with Clear Weather Silicone Sealant of approved make & backer rods complete as directed by Engineer-in-charge. Note : The bottom section to have drain hole arrangement with proper slope ). Window to be provided with locking arrangement , locakble from inside building; Good asthetic Aluminium grills covering outside window is also inclusive of scope Location: Ground Floor Window | Sqm | 102
8.03 | ADW 02 -A | Design, Supply, Fabrication and Fixing Aluminium Sliding Window , Powder coated to minimum 60 microns thickness (as per IS 7088) of Hindalco/Jindal or(or equivalent make) with two track sliding shutter in 5mm thick Clear Plain Glass of Saint Gobain make using for intermediate hooks duly fitted with standard accessories, fittings and EPDM siliconised gasket complete as per design, details and specification and approved by the EIC architect, including all hardware and consumables, sealing of joints with Clear Weather Silicone Sealant of approved make & backer rods complete as directed by Engineer-in-charge. Note : The bottom section to have drain hole arrangement with proper slope ). Window to be provided with locking arrangement , locakble from inside building; Aluminium grills are excluded in scope Location: First Floor Windows | Sqm | 102
8.04 | ADW 03 | Design, Supply, Fabrication and Fixing of Good asthetic Aluminium Door with frames ,Powder coated to minimum 60 microns thickness (as per IS 7088) of Hindalco/Jindal or(or equivalent make) with all standard accessories, fittings and EPDM siliconised gasket complete as per design, details and specification and approved by the EIC architect, including all hardware and consumables, sealing of joints with Clear Weather Silicone Sealant of approved make & backer rods complete as directed by Engineer-in-charge. Location- All Toilet doors | Sqm | 46.875
8.05 | ADW 04 | Design, Supply, Fabrication and Installation of Aluminium framed Ventilators of Hindalco/Jindal or any other approved make with Aluminium frames as per approved design & specification using aluminium extruded sections of 6063 grade alloy - along with other standard hardwares, fittings etc complete as per design, details and specification given in the drawing and approved by the architect , including all hardware and consumables all complete as directed. Fixed Louvers in Frosted Glass 4-5 mm thk as per the detailed drawings to be used duly adequate to withstand the wind load as per IS 875, complete as directed by the Engineer in Charge. The Aluminium profiles shall be powder coated with approved colour by architect. The thickness of powder coating shall not be less than 60 microns. The rate shall be inclusive of applying sealant, EPDM gasket,glazing clips ,necessary hardware and provision for exhaust etc complete. Location- toilets | Sqm | 6.75
8.06 | ADW 05 | Providing and fixing ACP panelling on wall ; Framing shall consist of Both ways horizontally and vertically on the wall / RCC/ Structural Steel members with Aluminium Sections of 2"x1" as directed by TSPL / EIC. This framing would be covered with 3mm thick "Aluminium Composite Panel" of desired colour & make of Alstrong included wooden or other decorative pattern and designs. The rate shall inclusive of necessary fixtures and fittings, sealant, ACP sheet etc. complete.Including At all Heights all inclusive. Location- Reception lounge, Staircase side walls, Outside Wall projections, Conference rooms- one side wall etc | SqM | 452
8.07 | ADW 06 | Providing and fixing Alstrong or equivalent make -Aluminium partition panels of thickness- 4.5mm of desired colour of EIC with all required aluminium frames & accessories. Location- Cabin to Cabin partition walls | SqM | 125
TOTAL FOR GLASS WORKS & ALUMINIUM /ACP WORKS
9.00 | ARC | ARCHITECTURAL FINISHING WORKS
9.01 | ARC 01 | Design, Supply, Fabrication and Installation of Fixed (Single Glass Unit) Glazing with Powder coated Aluminium frame Systems of Hindalco/Jindal(or equivalent make) as per approved design & specification using aluminium extruded sections of 6063 grade alloy -glazing unit panels being fixed as shown in the drawing and T6 tempered Glass 8 mm thk of Asahi/Modi/Saint Gobain make along with other standard hardwares, fittings etc complete as per design, details and specification given in the drawing and approved by the architect, including all hardware and consumables all complete as directed. | Sqm | 10
TOTAL FOR ARCHITECTURAL FINISHING WORKS
10.00 | MIS | MISCELLENEOUS WORKS
10.01 | MIS 01 | Providing and fixing of Mirror for Toilets of 8mm thick of approved quality with necessary bevelling to shape and pattern as per the detail drawing. The mirror shall be fixed to 25 x 25mm salwood frame work placed at 2'0'' c/c both ways, the frame work shall be cladded with 12mm thk plywood and finished with mirror using stainless "U"," L" and Z type running linear clips and 3M make double sided adhesive tape as per detail drawings. | Sqm | 14
10.02 | MIS 02 | Providing & fixing False ceiling at all heights / in all floors with Aluminium False ceiling with all materials as , cut to all shapes & size and in the required grid pattern supported on Powder coated aluminium frame work of approved make consisting of wall angles of section, bulbed Tees, main Tees, cross tees as per directions of EIC, including providing & fixing MS tab hangers, 6 mm dia MS standard suspenders of required height and providing necessary opening & additional frame work required for light & AC Duct fittings including provision for upturn as pelmets at ends along walls for return air in the false ceiling if required and painting the steel work with one coat of red oxide zinc chromate primer etc., complete all as per specification. Rate to include the provision for Trap doors ,drilling/cutting /providing holes for electrical fixtures /services and finishing the same . | Sqm | 1800
10.03 | MIS 03 | Supply,Fabricating & fixing in position MS window grills at all levels and heights for window openings considered at the rate of 1.5 Kgs per sft made of M.S square Bars including all the necessary fixtures,bolts and 2 coat of synthetic enamel paint over a coat of primer all as per the design and drawings provided as per the Architects /Engineers approval . The rate to include necessary welding wherever necessary as per the instructions at site. | Kgs | 500
10.04 | MIS 04 | Providing Flagging course around the building for plinth protection by laying Cement screed concrete 25mm thk as per (Item FLO 01) CM 1:6 (10-20mm thk ), etc all as per the architects instructions and approval.The sloping details to be as per the Architectural drawings/as per site conditions. | Sqm | 125
10.05 | MIS 05 | Providing & fixing Precast Concrete Slab 75-100mm thk for Duct cover as per details and drawings at all lvls & heights with scaffolding etc complete. | Sqm | Ro
10.06 | MIS 06 | Providing and fixing Poly Carbonate sheet for duct covering for all ducts with 50 x 50 x 6 mm angle as per the detailed drawings, including the necessary fixtures required etc., complete at all levels including all leads and lifts as per the instructions of Engineer in Charge. | Sqm | Ro
10.07 | MIS 07 | Providing & laying 20mm thk. Pre-polished Granite Urinal partitions of size as per the detailed drawing, polished on both side with bull nosing at exposed edges, including cutting groove in wall, finishing/grouting with cement mortor,making provision for fixing bolts and nuts, sealing the joints with sealant (Dow corning), curing, cleaning when ever instructed, pointing of joints with white/coloured cement, etc., complete with all leads & lifts at all levels &as per the instructions of Engineer in Charge. | Nos | 15
10.08 | MIS 08 | Providing, fabricating and erecting of Cat Ladders with all necessary Gusset Plates, Stiffener plates, Brackets, Bolts, Cleats, seating angles etc., to the required size, shape, alignment etc, as per the drawings. The quoted rate to include a coat of zinc chromate primer and two coats of Synthetic enamel painting etc., complete and as per the drawing and as directed by the Engineer-in-charge. | Ls | Ro
10.09 | MIS 09 | Providing and fixing Glass Canopy using 10mm thk Toughened glass of approved pattern, (Asahi / Saint Gobain/Modi make ) over pre installed MS framework (Cost of providing MS framework is part of Glass Canopy), including making suitable holes in the glass before installation complete as per design drawings. All the glass to glass joints shall be sealed with silicon weather sealant . The rates shall include for provding rain water drain,Silicon sealant grade shall be "Dow corning/GE Silicon,Enamel paint over a coat of primer etc as per the design requirement. | Sqm | Ro
10.10 | MIS 05 | Supply ,Fabrication and Installation of Aluminium Composite Panel with 4mm thk ACP sheets of Alcobond or equivalent make rivetted to the space frame as per the detailed drawings and also as per the manufacturers instructions and specifications ,duly adequate to withstand the wind load as per IS 875, complete as directed by the Engineer in Charge..The rate to include all fixing anchors,brackets,nuts ,screws ,bolts all consumables etc complete. | Sqm | Ro
10.11 | MIS 06 | Providing and fixing rolling type blinds for all windows with all accessories & fittings of approved make and design as per EIC instructions | SqM | 204
10.12 | MIS 07 | Stainless steel signage boards with letters engraved in black letters upto 6"height and signage over all sizes from 9" wide and lengh upto 24". | Nos | 40
10.13 | MIS 08 | Providing & fixing informatory Retro reflective sign board made of 3mm aluminum sheet various sizes maximum size 36 inhes x 36 inches as per EIC, etching with one coat of best quality epoxy primer and two coats of best quality epoxy paint, fixed on ,3.8mt long and 90mm dia.3mm thick MS stand post and frame fabricated from suitable size iron angle of 40x40x6mm and 10mm sq.bar painted with best quality epoxy coating in black and white bands. | Nos | 4
10.14 | MIS 09 | Plant Name and fixing logo and TSPL Plant letters in acryclic finish of different colour with samsung module lighting / strip lighting arrangement as per TSPL directions. All complete including switch to operate, wires, mounting on entrance canopy | SqM | 1.2
10.15 | MIS 10 | Providing & fixing good asthetic Canvas Fabric roof of standard make & color as directed by EIC for semi open dining | SqM | 100
TOTAL FOR MISCELLENEOUS WORKS
TOTAL - ARCHITECTURAL WORKS

## PHE
Schedule-A3
PHE WORKS - Servcie Building
Sl no | Description | Qty. | Unit | Rate | Amount
A | SANITARY FIXTURES
1 | Supplying,Installing , testing and commissioning white colour glazed wall hung European water closet with flush tank with all internal parts, fixing materials, pair of chair brackets, solid seat and cover with hinges and fixing screws, sealant ,WC connector , CP connecting pipes, angle valve,complete.
| Supply | 19 | Nos
| Installation | 19 | Nos
Cp fittings
2 | Supplying ,Installing testing and commissioning CP. Health faucet ( two in one) with flexible hose,CP Angle valve, wall flange, supporting hook with screws, fixing materials and sealant to all sides of wall flange complete.
| Supply | 19 | Nos
| Installation | 19 | Nos
3 | Supplying,Installing , testing and commissioning white color below counter oval wash basin with pair of C I supporting brackets duly painted with fixing screws or supporting screws as per manufacturers instructions, sealant for the joints, 1 no 15 mm long body bib cock, 1 nos CP inlet connection pipe with 1 no 15 mm C P angle valve, wall flanges, C P waste coupling, CP extension pipe up to wall , 1 no CP bottle trap , complete. ( counter sahll be prepared by other agencies)
| Supply | 10 | Nos
| Installation | 10 | Nos
4 | Supplying,Installing , testing and commissioning white color Rectangular wash basin with pair of C I supporting brackets duly painted with fixing screws or supporting screws as per manufacturers instructions, sealant for the joints, 1 no 15 mm long body bib cock, 1 nos CP inlet connection pipe with 1 no 15 mm C P angle valve, wall flanges, C P waste coupling, CP extension pipe up to wall , 1 no CP bottle trap , complete.
| Supply | R.O | Nos
| Installation | R.O | Nos
5 | Supplying ,Installing testing and fixing at the required height CP bibtap with wall flange, fixing materials and sealant to all sides of wall flange complete.
| Supply | 5 | Nos
| Installation | 5 | Nos
6 | Supplying, installing, testing and commissioning approved make white/ coloured integrated EPS urinals with 40mm C.P. dome type waste coupling 40mm C.P. bottle trap with C.P. extension pipe, 15mm dia solenoid valve unit & Battery operated sensor unit for automatic flushing with necessary electrical etc., C.P. spreader unit GI expansion bolts, including core cutting and water proofing etc.,
| Supply | 11 | Nos
| Installation | 11 | Nos
7 | Supplying and installing in position with all fixing materials for urinal partitions including all leads and lift complete
| Supply | 11 | Nos
| Installation | 11 | Nos
8 | Supplying ,and fixing in position approved make CP. Toilet paper holder , in executive toilets including fixing materials and sealant to all sides of wall complete.
| Supply | 19 | Nos
| Installation | 19 | Nos
10 | Installing, testing and commissioning of approved make stainless steel kitchen sink with , waste coupling of 32mm dia, with 190 mm long connection pipe, Sink cock with swinging wall mounted type spout, providing sealant alround the sink fixed to the counter complete.
Single bowl and single drain board : size: 800 / 500
Waste coupling shall be considered as per the sink type
| supply | 6 | Nos
| Installation | 6 | Nos
Make : Frankie
CP fittings :Jaquar
11 | Installing testing and commissioning C P shower unit comprising of single liver diverter, with mixer with provision for overhead shower , with spout, long bend pipe and wall flange, shower arm light body with wall flange complete.
| supply | 0 | Nos
| Installation | 0 | Nos
CP fittings : Jaquar/ Equivalent
Shower : Single liver diverter
Shower Head - -
Shower Arm -
12 | Supplying, installing , testing and commissioning approved make water heater of below mentioned capacity capable of withstanding high pressure ( up to 6.5 bar ) comprising of polypropelene body, built in pressure releif valve , non return valve , anti vaccum valve , drain velve , adjustable thermostat adjustable to 75 deg cen, and thermal cutout able to operate on 230V 50 HZ single phase supply covered with PUF insulation , CP connecting pipes, Cp angle valve of 15 mm dia , BUILT IN NRV all leads and lifts complete
| supply | 7 | Nos
| Installation | 7 | Nos
Make :
Model No:
CP fittings :
13 | Supplying , installing in position mirror near wash basin with ply wood backing and pvc beading all round with nfixing hooks all leads and lifts complete
| Size : 550 x 450 | 15 | Nos
14 | Supplying ,and fixing in position approved make CP TOWEL ROD 600 MM LONG toilets including fixing materials and sealant to all sides of wall complete.
| Supply | 9 | Nos
| Installation | 9 | Nos
Make
14 | Supplying ,and fixing in position approved make CP. GRAB BAR in physically challenged toilets including fixing materials and sealant to all sides of wall complete.
| Supply | 2 | Nos
| Installation | 2 | Nos
make of all sanitary ware : hindware and Cp fittings jaquar continental range
TOTAL OF SANITARY FIXTURES
B | INTERNAL SEWERAGE SYSTEM
1 | Supplying , installing , testing and commissioning approved make SWR P V C pipes conforming to IS 13592 TYPE ' B ' for soil and waste drainage system including necessary fittings, fixing and jointing material all leads and lifts, P C C support at all fittings and on straight run of pipes laid below ground or in sunken portion, OR providing hi-tech clamps to pipeson straight run , change in direction and for suspended floor traps for suspeded piping system including drilling for dash fasteners, anchor bolts, 10 mm GI threaded rods ( variable as per pipe dia ) to suit the site condition , nuts, bolts and washers as required , channels for supporting traps, all leads and lifts, complete.
Internal
| a) 75 mm dia | 90 | Rmt
| b) 110 mm dia | 110 | Rmt
Verticals
| a) 50 mm dia | 80 | Rmt
| b) 75 mm dia | 60 | Rmt
| c) 110 mm dia | 20 | Rmt
Ceiling
| a) 110 mm dia | 0 | Rmt
| b) 160 mm dia | 0 | Rmt
Make : Astral
2 | Supplying , installing , testing and commissioning approved make u P V C pressure pipes ( 6 kg/sqcm)conforming to IS 4985 for waste drainage system including necessary fittings, fixing and jointing material all leads and lifts complete.
| a) 40 mm dia | 15 | Rmt
| b) 50 mm dia | 10 | Rmt
Make : Astral
3 | Supplying , installing, testing and commissioning pvc inlet floor trap conforming to IS 3989 with required P C C support placed to required level as per site condition, CP grating, complete.
| a) 110 mm dia for floor trap and 75 mm dia outlet | 25 | Nos
| b) P trap | 2 | Nos
Make : Astral
4 | Supplying,fabricating and placing in position M S angle supports ( to fix the watersupply and drainage lines) in shafts, on walls, below ceiling,below soffit of beams with a coat of red oxide primer and two coats of approved colour of enamel paint including all leads and lifts, required scaffolding, complete. | 300 | Kgs
5 | Making openings in beams/ slabs to draw water supply and draiange lines by core cutting with mechanical equipment only.
| In beams 200 mm x 150 mm | 0 | Nos
| In slab 100 mm dia | 0 | Nos
| In slab 150 mm dia | 50 | Nos
| In retaining wall | R.O | Nos
6 | Providing Grout to the openings in beams/ slabs made to draw water supply and draiange lines by core cutting with mechanical equipment and filling the annular space with chemical grout as per manufacturers recommendation and to attain leakless joint complete with all l;eads and lifts.
| In beams 200 mm x 150 mm | 0 | Nos
| In slab 100 mm dia | 50 | Nos
| In slab 150 mm dia | 0 | Nos
| In retaining wall | R.O | Nos
7 | Supplying installing testing and commissioning approved make oil and grese trap with required inlets and outlets all leads and lifts complete.
| Make : Aco | 0 | Nos
TOTAL FOR INTERNAL SEWERAGE SYSTEM
C | WATER SUPPLY SYSTEM - DOMESTIC
1 | Supplying, installing testing of approved make medium quality CPVC SDR 11 pipes manufactured to meet the requirements of ASTM-D 2846and higher dia of pipes in SCH 40 and SCH 80 as per ASTM F441 and fittings as per ASTM F 439 with all specials such as bends, tees etc., including necessary cutting,solvent welding fixing on walls, laying below ground etc.,The quoted rate shall include for chasing the walls, making bores in walls and making good the chased surfaces in cement mortar 1:3, etc. complete
Internal
| a) pipe size 15 mm | 40 | Rmt
| b) pipe size 20 mm | 120 | Rmt
| c) pipe size 25 mm | 30 | Rmt
| d ) pipe size 32 mm | 50 | Rmt
| e ) pipe size 40 mm | R.O | Rmt
| f ) pipe size 80mm at ground level | 0 | Rmt
Vertical
| (a) pipe size 25 mm | 50 | Rmt
| (b) pipesize 50 mm | 80 | Rmt
| c) 65 mm dia | 0 | Rmt
Terrace
| (a) pipesize 50 mm | 50 | Rmt
bore well to sump - approximate
| imate | 0 | Rmt
UG sump to oht - approximate
| (a) pipe size 65mm dia | 0 | Rmt
Municipal line to sump - approximate
| (a) pipe size 65mm dia | 0 | Rmt
Tanker line to sump - approximate
| (a) pipe size 100 mm dia | 0 | Rmt
Make : astral
2 | Supplying, Installing , testing and commissioning approved make concealed stop cock with necessary fixing materials, wall flange complete.
| a) 20 mm (Internal dia) | 10 | Nos
3 | Supplying, Fixing approved make gun metal Ball valve to suit the diameter including necessary fittings etc.complete
| a) 15 mm dia | R.O | Nos
| b) 20 mm dia | 5 | Nos
| c) 25 mm dia | 0 | Nos
| d) 40 mm dia | 5 | Nos
| e) 50 mm dia | 5 | Nos
Make : VB
4 | Supplying fixing testing and commissioning of approved make slim seal butterfly valves with necessary flanges nuts, bolts neoprene rubber gaskets complete confirming to I S 13095 : 1991 specifications.
| a) 65 mm dia | 0 | Nos
Make : VB
5 | Supplying, Fixing approved make gun metal Non return valve to suit the diameter including necessary fittings, etc.complete
| a) 65 mm dia | 0 | Nos
| b) 50 mm dia | 2 | Nos
Make : VB
6 | Supplying, installing, testing and commissioning of submersible electrical driven pump to lift domestic water with all necessary arrangements to operate on 3 PH 50 HZ, 440V AC supply fitted on a common base frame accessories to lift the pump during maintenance , control panel with wiring from TPN switch to control panel and to the pump and the control panel comprising of O/L relays, single phase preventor,separate overload trip and relayset, ON/OFF/TRIP indicating lamps,start/stop push buttons etc., complete as complete. | approximate qty and spec
Duty of the Pump
| 2.0 lps at 25 m head (1 W+ 1st.by = 1No set) | 1 | Set
Storm water sump pump with solid handling capacity of 3 mm
Make : Grundfoss
7 | Supplying, Installing testing and commissioning approved make water level controller with cabling in P V C conduit ( 3 core & multi strand copper wire 1.5 sq mm) and automatic water level indicator digital type, indicating the level of water in percentage with 6 core multistrand 1.5 sqmm wire in P V C conduit. The controller to operate on 440V with a circuit supply of 9V DC and probe voltage of 12 V AC, 5A relay 2nos,the probes shall be made 304 grade S S molded in high impact P V C, all enclosed in a powder coated die folded sheet metal box.etc complete,from the control panel, U G sump TPN switch and OHT. | 1 | Nos
| Length of cable | 80 | Rmt
| Length of conduit | 80 | Rmt
make : Sri Vinayaka
8 | Providing and constructing water meter chamber over a bed of P C C 1:4:8,in 200 mm thick solid block in C M 1:8, both internal and external plastering in C M 1:6, medium duty precast concrete cover with all leads and lifts, including curing complete. | 1 | Nos
Size of chamber 750 X 750 x 600 mm clear
9 | Providing and constructing inspection chamber ( for bore well) with first quality table molded bricks of standard size in C M 1:6 over a P C C bed of 1 4 8 of 100 mm thick, internal surface plastered smooth and externally finished rough including providing P C C for channeling and providing pre cast slab of 100 mm thick with frame and cover including curing all leads and lifts fixing in position fiber coated steps etc., complete. | 1 | Nos
10 | Supplying, Fixing approved make pressure reducing valve with pressure guage and stop valves assembly to suit the diameter including necessary fittings, etc.complete
| a) 50 mm dia | 0 | Nos
Make : Honeywell
11 | Supplying , installing in position fabricated GI , MS and P V C puddle flanges as per the drawing with the required length , tieing in position with the reinforcement , hot dip galvanising for MS and GI puddle flanges with all leads and lift complete.
OVER HEAD WATER TANK
DOMESTIC WATER STORAGE TANK
| Over flow 500 mm dia | 1 | Nos
Air vent 65 mm dia with mosquito proof
| mesh | 1 | Nos
| Medium duty C I manhole frame and cover of size 600 x 600 | 1 | Nos
| Outlet 50 mm dia | 1 | Nos
| Drain pipe 50 mm dia | 1 | Nos
ALL THE ABOVE SPECIFIED PUDDLE FLANGES ARE
500 MM MINIMUM IN LENGTH
U G SUMP
ALL THE ABOVE SPECIFIED PUDDLE FLANGES ARE
500 MM MINIMUM IN LENGTH
Pump outlet
| UG Sump to OHT 50 mm dia from treated water tank | 1 | Nos
| 19 mm dia P V C conduit 300 mm long | 1 | Nos
12 | Supplying , installing in postion approved make PVC water tank with inlet outlet , P C C pedestal to support the tank of below mentioned capacity with all ledas and lifts complete
| capacity 5000 ltrs | 1 | Nos
TOTAL FOR WATER SUPPLY SYSTEM-DOMESTIC
D | RAIN WATER SYSTEM
1 | Supplying , installing , testing and commissioning approved make SWR P V C double socketed pipes conforming to IS 13592 TYPE ' B ' for rain water system including necessary fittings, fixing and jointing material all leads and lifts, P C C support at all fittings and on straight run of pipes laid below ground complete.
Terrace
| a) 110 mm dia | 60 | Rmt
| b) 75 mm dia | 90 | Rmt
Total PHE WORKS

## LPS
Schedule-A4
LIGHTNING PROTETION SYSTEM - Servcie Building
S.NO. | DESCRIPTION OF WORK | QTY | UNIT | RATE | AMOUNT IN RS
A1 | LIGHTNING PROTECTION SYSTEM :
1 | Supply & erection of vertical air terminations
as specification complete.
| SUPPLY | 2 | Set
| ERECTION | 2 | Set
A3 | EARTH PIT STATIONS
Providing the earth pit stations with necessary materials, labour, civil works, etc. as per Indian Standard specification IS:3043 etc. complete.
1 | 3 mtrs long 50 mm dia. G.I pipe
electrode earth station.The chamber size
shall be 450 x 450 mm with C.I. Cover
plate. The identification number shall
be provided both inside and outside.
| SUPPLY | 4 | Each
| ERECTION | 4 | Each
2 | 600 x 600 x 3.15 mm copper plate
electrode earth station.The chamber
size shall be 450 x 450 mm with C.I.
Cover plate. The identification number shall be
provided both inside and outside of equipment.
| SUPPLY | RO | Each
| ERECTION | RO | Each
A4 | HORIZONTAL / DOWN CONDUCTORS
1 | 25 x 3 mm GI tape (Hot dip galvanised) for horizontal / down conductors as per specification.
| SUPPLY | 200 | Mtr
| ERECTION | 200 | Mtr
2 | 40 x 6 mm GI tape (Hot dip galvanised)
| SUPPLY | 50 | Mtr
| ERECTION | 50 | Mtr
3 | 25 x 6 mm GI Tape (Hot Dip Galvanized)
| SUPPLY | R,O | Mtrs
| ERECTION | R,O | Mtrs
4 | Supply & erection of 70Sqmmflexible Copper cable for down conductors as per specification.
| SUPPLY | R,O | Mtr
| ERECTION | R,O | Mtr
A5 | TEST LINKS
1 | Test links as per specification grouted to wall at 1200mm above ground level complete with all fixing accessories etc., complete
| SUPPLY | 2 | Each
| ERECTION | 2 | Each
A | TOTAL FOR ESE LIGHTNING PROTECTION SYSTEM |  |  |  | 0

## IT LAN
Schedule-A5
IT NETWORKING , CCTV & LAN JOBS - Servcie Building
S.NO. | DESCRIPTION OF WORK | QTY | UNIT | Make | RATE | AMT IN RS
A | IT networking :
A1 | LAN CABLES :
| Supply & laying & termination inclusive of all accessories of LAN cables network to create connectivity with each work stations, open cubicles & closed cabins & in other strategic locations like lounge, meeting rooms, TP rooms etc | 10 | Box | D-Link
A2 | CIVIL WORKS FOR OUTDOOR CABLE LAYING :
A2.1 | Preparation of outdoor cable trenches including excavation,back filling,sand filling,cable tiles,compaction as per specification of the for the following sizes. | 3 | BOX | D-Link
A2.2 | CHAMBER BOXES
Construction of chamber box of following sizes complete with heavy gauge plate.
1 | 300mmX300mm wide & depth 450mm. | R,O | No's
A4 | TELEPHONE/LAN SOCKETS :
Supply & erection of Telephone/LAN
socket outlet comprising of Top plate with
RJ-45 outlets AMP/AVAYA(LUCENT) certified with
Plastic moulded boxes.The scope shall
include structured cabling system for computer
complete etc., as required.The installation shall
include cost of crimping,any accessories required
1 | Cat 5E Information outlet (RJ-45) Single (I/O with SMB) |  |  | Molex
| SUPPLY | 200 | No
| ERECTION | 200 | No
2 | Ethernet Patch Cat 6 7 feet
| SUPPLY | 200 | No
| ERECTION |  | No
3 | Ethernet Patch Cat 6 3 feet |  |  | Molex
| SUPPLY | 200 | No
| ERECTION | 200 | No
4 | FIBER PATCH PANEL,LIU,24P Fully loaded |  |  | Molex
| SUPPLY | 8 | No
| ERECTION | 8 | No
6 | 42U Floor mounted communication rack with front glass door,power manager,cable manager,hardware.
with wheels,castors along with ex-fans
| SUPPLY | 1 | No | Netrack/APW
7 | 12U Wall mounted communication rack with front glass door,power manager,cable manager,hardware. |  |  | Netrack
| SUPPLY | R.O | No
8 | 9U Floor mounted communication rack with front glass door,power manager,cable manager,hardware.
with wheels,castors along with ex-fans
| SUPPLY | R.O. | No | Netrack/APW
9 | Cat5e 24 Port Patch Panel
| SUPPLY | 8 | No | Molex
A6 | DUMMY CONDUITS FOR DATA ,LAN, TELEPHONE & TV:
1 | 19 mm dia, FRLSPVC conduit with all accessories.(For IT LAN)
| SUPPLY | 3000 | Mtr
| ERECTION | 3000 | Mtr
3 | 25 mm dia, FRLSPVC conduit with all accessories.(For lan & tel)
| SUPPLY |  | Mtr
| ERECTION |  | Mtr
4 | 1" casing & capping
| SUPPLY | 20 | Mts
| ERECTION | 20 | Mts
5 | 1and 1/2" casing & capping
| SUPPLY | 20 | Mts
| ERECTION | 20 | Mts
6 | 1" metal reinforced pvc flexible pipe.
| SUPPLY | R.O. | Mts
| ERECTION | R.O. | Mts
A7 | FIBRE
1 | 24 Core Outdoor Multimode Fibre Optic Cable
| SUPPLY | R.O. | Mtr. | Molex
2 | 12 Port Rack Mount LIU
| SUPPLY | R.O. | Nos. | Molex
3 | SC Connectors
| SUPPLY | 8 | Nos. | Molex
4 | SC Couplers
| SUPPLY | 8 | Nos. | Molex
5 | SC to LC/MtRJ Duplex Patch Cords
| SUPPLY | 10 | Nos. | Molex
6 | SC to SC Duplex Patch Cords
| SUPPLY&TERMINATION | R.O. | Nos. | Molex
A8 | MANAGED SWITCH
1 | 12 Port Core Switch (Layer 3) 10/100/1000 Mbps
| SUPPLY&ERECTION | R.O. | Nos. | Cisco
2 | Redundant Power Supply for Core Switch
| SUPPLY&ERECTION | R.O. | No. | Cisco
3 | 4 Slot GBIC Module
| SUPPLY&ERECTION | 1 | No. | Cisco
4 | SX Module
| SUPPLY&ERECTION | 4 | No. | Cisco
5 | 24 Port 10/100Mbps + 4 GBIC Ports Managed Switch(WS2960S-24PSL
| SUPPLY&ERECTION | 4 | No. | Cisco
6 | 48 Port 10/100Mbps + 4 Port 10/100/1000 Managed Switch
| SUPPLY&ERECTION | R.O. | No. | Cisco
A9 | CCTV / Biometric controlled Access System
1 | CCTV cameras at essential locations. High definition 360Degree CCTV camera with all accessories, networking, hardware and software required for interfacing with existing CCTV network (all cameras shall be of IP based &accessible on http protocol)
| i. Outdoor Make- Bosch, Type- PTZ (Pan, Tilt -360Deg , Zoom ), Auto Dome | 3 | Nos. | Bosch
IP STARLIGHT 7000 HD, Protocol- http based
| ii. Indoor Make- Bosch, Type- Flexi Dome, Indoor 4000HD & Protocol- http based | 7 | Nos. | Bosch
2 | Providing & fixing Biometric based access control on all the entry door points of the building beyond visiting lounge | 3 | Nos. | Saviour / make as suggested by TSPL
A10 | Metallic Wireways/Raceways:
Supply, fabrication and erection of
raceways, made out of 1.6mm thick M.S.powder coated
sheet with top cover . The race way will
be run below the Beam level & fixed to supporting structure by means of 'U'clamps.
The MS sheets shall be surface treated such as
phosphating, pickling etc and painted
with approved colour of paint. The race
way shall be complete with
interconnection piece, top cover, fixing
screw, nut, bolts etc., Sample to be
approved by consultants before
fabrication. These raceways will be used as wiring
ways/lighting raceways for fixing Light fitting & Fans,
NOTE:.The supply for supporting structure & 'U' clamps should be taken under the heading " Steel Items'
1 | 300m wide x 25mm depth Metallic powder coated Raceways.
| SUPPLY | 200 | Mtr
| ERECTION | 200 | Mtr
2 | 300mm X 300mm x 25mm depth Metallic powder coated Junction box.
| SUPPLY | 20 | Each
| ERECTION | 20 | Each
TOTAL IT / LAN COST

## Lighting
Schedule-A6
Lighting WORKS (LED fixtures only to be used)
(Contract is on EPC lumpsum basis & Items for execution shall be selected as per below brief specifications/ line items)
S.NO. | DESCRIPTION OF WORK | QTY | UNIT | RATE | AMOUNT IN RS
A | CIRCUIT MAINS :
A1 | Supply and running of 1100 V grade PVC
insulated copper conductor wires in minimum
2mm thick PVC conduits as per specification titled
"DISTRIBUTION SYSTEM, CONDUITS, WIRING
AND ACCESSORIES" and following details.
The rate shall include supply and
installation of all materials like
conduits, wires, fixing accessories,
etc. as detailed in Clause of above
mentioned specification.
1 | Supply and laying of 2 Runs of single core 2.5Sq.mm and 1 Run of single core 1.5Sqmm PVC insulated multistrand copper conductors in 1 No. of 25mm dia PVC conduits with all necessary accessories/ JBs complete as required.
| SUPPLY | 1500 | Mtrs |  | 0
| LAYING | 1500 | Mtrs |  | 0
A | TOTAL FOR CIRCUIT MAINS |  |  |  | 0
B | POINT WIRING : FOR LIGHTS, SOCKETS & FANS.
B1 | Wiring with 2 x 2.5 Sqmm FRLS insulated 1100V
grade copper conductor wires and 1 x 1.5 Sqmm
PVC insulated FRLS earth wire in 2mm thick, 25 / 19mm PVC
conduits as per specification titled
"DISTRIBUTION SYSTEM, CONDUITS, WIRING &
ACCESSORIES". Scope shall include all wiring materials, switches, sockets, regulator, fan hook box, & switch box complete .
(SWITCHES SHALL BE MODULAR)
1 | Single light point controlled by a 6 Amps. switch.
| SUPPLY | 50 | Nos |  | 0
| ERECTION | 50 | Nos |  | 0
2 | Two light point controlled by a 6 Amps. switch.
| SUPPLY | 60 | Nos |  | 0
| ERECTION | 60 | Nos |  | 0
3 | Three light point controlled by a 6 Amps. switch.
| SUPPLY | 40 | Nos |  | 0
| ERECTION | 40 | Nos |  | 0
4 | Four light point controlled by a 6 Amps. switch.
| SUPPLY | 20 | Nos |  | 0
| ERECTION | 20 | Nos |  | 0
5 | Five light point controlled by a 6 Amps. switch.
| SUPPLY |  | Nos
| ERECTION |  | Nos |  | 0
6 | Six light point controlled by a 6 Amps. switch.
| SUPPLY |  | Set |  | 0
| ERECTION |  | Set |  | 0
7 | Single light point controlled by 2-way 6 Amp, switch.
| SUPPLY | 5 | Nos |  | 0
| ERECTION | 5 | Nos |  | 0
7 | Two light point controlled by 2-way 6 Amp, switch.
| SUPPLY |  | Nos |  | 0
| ERECTION |  | Nos |  | 0
7 | Three light point controlled by 2-way 6 Amp, switch.
| SUPPLY |  | Nos |  | 0
| ERECTION |  | Nos |  | 0
7 | Fourlight point controlled by 2-way 6 Amp, switch.
| SUPPLY |  | Nos |  | 0
| ERECTION |  | Nos |  | 0
8 | Ceiling Fan points (with fan hook Box)
including 6 Amp single pole control switch.
| SUPPLY |  | Nos |  | 0
| ERECTION |  | Nos |  | 0
9 | Call bell & bell push point.
| SUPPLY |  | Nos |  | 0
| ERECTION |  | Nos |  | 0
10 | Exhaust fan point with wall mounted 5
amps 3 pin socket near fan location and
6 Amps single pole controlling switch
located independently. The rate shall
also include supply of 6 Amps, 3 pin plug.
| SUPPLY | 10 | Nos |  | 0
| ERECTION | 10 | Nos |  | 0
11 | 1 no 6A 3 pin socket and switch Connected to lighting circuits ( Dependent)
| SUPPLY | 10 | Nos |  | 0
| ERECTION | 10 | Nos |  | 0
12 | 2 or 3 No. 6A 3 pin socket and switch Connected to lighting circuits ( Dependent)
| SUPPLY | 10 | Nos |  | 0
| ERECTION | 10 | Nos |  | 0
13 | 16 Amps, 3-pin (250 Volts) single phase universal shuttered socket with an independent 16 A Switch/ 16A MCB as per EIC directions (Independent point) for geaser at toilet, kitchen points etc
| SUPPLY | 15 | Set |  | 0
| ERECTION | 15 | Set |  | 0
B | TOTAL FOR POINT WIRING |  |  |  | 0
C | SUPPLY OF LIGHTING FIXTURES
LAMPS/CEILING FANS/EXHAUST FANS.
SUPPLY OF INDOOR / OUTDOOR LIGHTING FIXTURES /FANS
Supply & Erection of the following type light fixtures complete with all accessories, chains, hangers etc. complete as required. All light shall be of energy saving LED type only with standard make- Bajaj, Wipro, phillips ; Inside building - All working area inside building shall have average illumination level in LUX as 400, non working areas like kitchen, canteen, stores,documentaionn room , toilet shall have LUX level of 150-200; Outdoor / landscaping, road way , pathways shall have LUX level of 15-20 .LUX level design with contour map shall be submitted by contractor before finalising Quantity
C1 | General Lighting & Car Parking
1 | 1 X 36/18W Mirolta Patti LED type Tubelight having white
end caps & accessories with lamp
| SUPPLY | 30 | Nos |  | 0
| ERECTION | 30 | Nos
2 | 2X2 feet high asthetic sky Lights LED (24/50 watts) suitable for all false ceilings
| SUPPLY | 177.7778 | Nos |  | 0
| ERECTION | 178 | Nos
3 | IP55 class Outdoor LED flood light- 100/ 150W
| SUPPLY | 20 | No |  | 0
| ERECTION | 20 | No
4 | 1 x12 Watts IP55 class, good asthetic, Circular type down lighter/ wall light with LED Lamps suitable for canopies & projected slabs
| SUPPLY | 30 | Nos |  | 0
| ERECTION | 30 | Nos
5 | Providing and fixing Outdoor CAST IRON DECORATIVE Heritage finish Lamp Post design approved at per EIC (Dwaraka India or Equalent). Incuding all arrangment to fix pole, LED lamp and cable to make it functional. This ligting shall be provided at connecting road ways
| SUPPLY | 5 | Nos |  | 0
| ERECTION | 5 | Nos
5 | Led Bollard , aluminum Die cast body to be provided in all Divider, pathways and landscaping
| SUPPLY | 30 | Nos |  | 0
| ERECTION |  | Nos
9 | Supply & Installation of Industrial Type Emergency LED Light (14-18W) with Exit Sign(minimum 1HrBack Up arrangement)
| SUPPLY | 8 | Nos |  | 0
| ERECTION |  | Nos |  | 0
10 | Emergency LED lamp with in built inverter & 1 hour battery - to be provided for 5% LUX level in each inside building areas, one per meeting room, conference room, closed cabins
| SUPPLY | 10 | No |  | 0
| ERECTION | 10 | No
11 | Chandilier fixture
| SUPPLY |  | No |  | 0
| ERECTION |  | No |  | 0
C2 | CEILING FANS:
Supply & Erection of white colour ceiling fan
with double ball bearings, accessories, connecting
wire and other standard accessories but
excluding regulator in all sitting places
1 | 1200mm Sweep, 3 blade ceiling fan.
| SUPPLY | 50 | Nos |  | 0
| ERECTION | 50 | Nos |  | 0
2 | 300 Watts electronic regulator.
| SUPPLY | 50 | Nos |  | 0
| ERECTION | 50 | Nos |  | 0
C3 | EXHAUST FANS:
Supply,Erection of exhaust fans with
sheet metal blades, necessary brackets,
anti-corrosive epoxy painting, rubber
cushions, etc. The 5 Amps 3-pin socket
near fan location & remote located
single-pole controlling switch, are
included in the point wiring for exhaust fan point.
1 | 300 mm impeller dia, 1400 rpm exhaust
fan (single phase)
| SUPPLY | 10 | Nos |  | 0
| ERECTION | 10 | Nos |  | 0
C | TOTAL FOR INTERNAL LIGHTING/FANS/EXHAUST FANS |  |  |  | 0
D | EXTERNAL LIGHTING SYSTEMS
NOTE: THE RATE QUOTED SHOULD INCLUDE
THE COST OF LAMP ALSO.
D1 | STREET LIGHTING
1.1 | Supply,Erection of
GI. Tubular Pole of 9mts length (7.5mtrs above ground) with single arm with all the required accessories.including excavation, concrete foundation, wiring from pole base to fixture including Hensalmake termination box etc.
| SUPPLY | R.O. | Nos |  | -
| ERECTION | R.O. | Nos |  | -
2 | LED outdoor street light fixture with all accessories - selection of Wattage shall be as per illumination level study to achieve 20LUX
with control gear etc, complete , Mounted on the above pole .
| SUPPLY | R.O. | Nos |  | -
| ERECTION | R.O. | Nos |  | -
D | TOTAL FOREXTERNAL LIGHTING FIXTURES. |  |  |  | 0
A B S T R A C T
A | CIRCUIT MAINS : |  |  |  | 0
B | POINT WIRING |  |  |  | 0
C | INTERNAL LIGHTING/FANS/EXHAUST FANS |  |  |  | 0
D | EXTERNAL LIGHTING FIXTURES. |  |  |  | 0
| GRAND TOTAL |  |  |  | 0

## Electrical
Schedule-A7
Electrical works for Power Supply
(Contract is on EPC lumpsum basis & Items for execution shall be selected as per below brief specifications/ line items)
S.NO. | DESCRIPTION OF WORK | QTY | UNIT | RATE | AMOUNT IN RS
A | MEDIUM VOLTAGE SWITCH BOARDS & Other Equipment:
A1 | Supply and installation of Distributation Panel at Firestation (IP-65, 2mm CRGA GI Power Coated sheet, 450 mm Ground Clearance, sheet metal fabricated, powder coated, having dust-proof and vermin 'proof, gasketed and hinged door with two Incommer & one Buscoupler with protection. 1. Incommer of MCCB 415V, 630A-2 No's 2. Bus Coupler of MCCB 415V, 630A-1 No 3. Outgoing Feeder MCCB-415V, 160A-5 No's 4. Outgoing Feeder MCCB -415V, 63A-10 No's 5. Outgoing Lighting Feeder (with 3-Ph,4 wire Lighting Transformer 5 KVA)-415V, 63A-2 No's 6. Multi function energy meter of 0-500A with CT, 0-500V rating as per make(L&T/Converse/ Rishabh / Secure)- 2 Nos at incomers 7. 4 Runs of copper insulated Busbar & other power accessories as required to withstand- 500A , 500V " 1 Nos "MCCB/MCB- scheider,ABB, Siemens MFM- L&T/Converse/ Rishabh / Secure | No | 1 |  | 0
A2 | Switchboards/ panels/ PDB's as per specification
titled "415 Volts Switch Boards", as per approved schematic
drawing complete as required. Supply and
fixing of steel supporting channels shall be
measured separately under the heading "Steel
Items". Grip bolts required for fixing on to
floors will also be measured separately.
1 | HVAC PANEL
| SUPPLY | 1 | Set |  | 0
| ERECTION |  | Set |  | 0
4 | UPS O/P PANEL
| SUPPLY | 1 | Set |  | 0
| ERECTION |  | Set |  | 0
A3 | Supply installation & Commissioning of 15KVA UPS System with 4Hr's back Up Power Supply(including VRLA batteries) of Make-/Emerson/Hitachi2 Nos APC/DB Power/Emerson/Hitachi | 1 | set |  | 0
A4 | Supply and installation of complete fire alarm system as per TAC with all arrangement of cablmes 2 core 1.5 sq.mm armoured. The scope include main alarm panel with display , hooters and wiring to all fire detection system. Make shall be of GE- Edwards & compatiblity & cabling to connect with existing plant fire alarm system at CCR to be provided.Approvals from TAC during drawing stage & commisisoning stage shall be in contractor's scope | 1 | set |  | 0
1 | S&I of Photo electric(Optical) type Smoke Detector with flashing LED Below/above the false ceiling where ever required as per IS standard. | 90 | Nos |  | 0
2 | S&I of Heat Detector with flashing LED above the false ceiling where ever required as per drawings and as per IS standards | 90 | Nos |  | 0
3 | supply and installation of response indicators for above ceiling smoke detectors. All inclusivs to make it functional | 90 | Nos |  | 0
4 | Providing , laying with wrapping coating in underground/ painted above ground with supports -Hydrant point with fire hose with box etc, 2 number per floor or as per TAC norms by arranging tapping point from existing hydrant network nearby area.
4a | 150 NB,6.0mm thick, operating pressure -8Kg/Cm2 MS line supply & laying with wrapping coating underground or with 120 micron painted surface above ground with hydrant water medium; | 500 | M |  | 0
4b | 80 NB,4.0mm thick, operating pressure -8Kg/Cm2 MS line supply & laying with wrapping coating underground or with 120 micron painted surface above ground with hydrant water medium for branching inside building or at terminal point; | 150 | M |  | 0
5 | Supply , installation of industrial type RO system for water pruification with 50LPH caapcity & 20 L in built storage tanks of Kent or Eureka Forbes make | 3 | Nos |  | 0
6 | Design, supply & installation of Centralised Air condition system suitable for complete Admin service building with all equipment, system, control panel , blowers, Ducting,under deck unsulation of all building roof, chiller/ Air handling units , piping etc suitable for false ceiling office & dining area of 1500 SqM | 1 | Lumpsum |  | 0
7 | S & I of point wiring for music - cum Public Address system comprising of 2x 1.0 sqmm stranded , copper conductor , flexible PVC insulated and PVC Sheathed wire pulled through 20 mm dia .PVC heavy gauge conduits and looped from one speaker to other and to the volume control and control switch wherever applicable and finally terminated at Tag Block.PA system Mike control shall be provided in Receptionist desk & another one location ; Speakers shall be provided flushed in false ceiling at all cabins, work station areas & lounge | 1 | Lot |  | 0
8 | Providing & fixing 230V, 2 KW electrical Geaser for toiler areas | 5 | Nos |  | 0
A | TOTAL FOR DBs & Electrical equipments/ systems |  |  |  | 0
B | FACTORY-BUILT MCB DISTRIBUTION BOARDS:
Supply, store, erection, testing and
commissioning of MCB Distribution
Boards, wall-mounted (either surface or
recessed type)as per schematic drawings.
The erection rates shall include fixing
of DB on wall including supply of all
fixing accessories, civil works etc.
Space provision shall be made for
mounting 30mA ELCB in the incomer MCB. The
rate shall be same for any combination
of outgoings TP/SP.
B1 | VERTICAL TYPE. DOUBLE DOOR TPN DB :
1 | 12 Way TPN DB with seperate Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
2 | 8 Way TPN DB with seperate Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
3 | 4 Way TPN DB with seperate Incomer of approved make
| SUPPLY | 3 | Each |  | 0
| ERECTION | 3 | Each |  | 0
B2 | VERTICAL TYPE. DPX MCCB TPN DB :
1 | 8 Way TPN DB with seperate Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
B3 | HORIZONTAL TYPE. DOUBLE DOOR TPN DB :
1 | 8 Way TPN DB with seperator Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
2 | 6 Way TPN DB with seperator Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
3 | 4 Way TPN DB with seperator Incomer of approved make
| SUPPLY | 7 | Each |  | 0
| ERECTION | 7 | Each |  | 0
B4 | SINGLE PHASE DB WITH DOUBLE DOOR
1 | 12 Way DB with seperator Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
2 | 8 Way DB with seperator Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
3 | 6 Way DB with seperator Incomer of approved make
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
B4 | MCB, ELCB, ELMCB
Supply, store, erection, testing and commissioning of
the following MCB,s, ELCB,s & ELMCB,s of motor duty,
C-curve charcterstics Din rail mounted to be fixed in the above MCB Distribution Boards to suit any required combinations specified in the riser diagrams. With all the required accessories.
1 | 4-pole Residual current circuit breaker (RCBO) with
normal current rating of 40Amps & sensitivity of 100mA.
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
2 | 2-pole Residual current circuit breaker (RCBO) with
normal current rating of 20Amps & sensitivity of 100mA.
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
3 | 6-32 Amps SP MCB
| SUPPLY | 120 | Each |  | 0
| ERECTION | 120 | Each |  | 0
4 | 40-63 Amps SP MCB
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
5 | 6-32 Amps DP MCB
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
6 | 40-63 AmpsTPN MCB
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
7 | 6-32 Amps TPN MCB
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
8 | 6-32 Amps 4P MCB
| SUPPLY | 4 | Each |  | 0
| ERECTION | 4 | Each |  | 0
9 | 40-63 Amps 4P MCB
| SUPPLY | 6 | Each |  | 0
| ERECTION | 6 | Each |  | 0
B | TOTAL FOR FACTORY-BUILT MCB DISTRIBUTION BOARDS |  |  |  | 0
C | POWER AND CONTROL CABLES : (Terminal point shall be at Main plant common switchgear at TG building & approximate route length of incomer cable shall be 500M & 2 Runs supply & laying covered in scope
C1 | Supply&Laying , providing Double compression brass cable glands,lugs and testing of 1.1 KV
Grade XLPE/PVC insulated Copper/Aluminium conductor
steel armoured power cables(AYFY) as per
specification & make of KEI, Universal cables, RR & Havells. The rates quoted shall
be for laying in trays/ cable trenches
(indoor and outdoor), pipes, etc. For
buried cables, the excavation work will
be included under the heading "Civil
works for outdoor cable laying." Party to use top covered cable tray or GI conduit for above ground areas
1 | 3.5 Core x 300 Sqmm Armoured Cable (XLPE) from main plant TG buidling Switchgear to service building DB
| SUPPLY | 1000 | Mtr |  | 0
| LAYING & termination | 1000 | Mtr |  | 0
7 | 3.5 Core x 70 Sqmm armoured Al. Cable (XLPE).
| SUPPLY | 300 | Mtr |  | 0
| LAYING & termination | 300 | Mtr |  | 0
8 | 3.5 Core x 50 Sqmm Cable (XLPE).
| SUPPLY |  | Mtr |  | 0
| LAYING & termination |  | Mtr |  | 0
9 | 3.5 Core x 35 Sqmm Cable (XLPE). for distribution inside building from MDB to all sub- DBS
| SUPPLY |  | Mtr |  | 0
| LAYING & termination |  | Mtr |  | 0
10 | 4 Core x 25 Sqmm Cable (XLPE). for distribution inside building from MDB to all sub- DBS
| SUPPLY |  | Mtr |  | 0
| LAYING & termination |  | Mtr |  | 0
11 | 4 Core x 16 Sqmm Cu Cable (XLPE). for distribution inside building from MDB to all sub- DBS
| SUPPLY | 300 | Mtr |  | 0
| LAYING & termination | 300 | Mtr |  | 0
12 | 4 Core x 10 Sqmm Cu Cable (XLPE).external lighting for distribution inside building from MDB to all sub- DBS / street lighting/ outdoor power supply
| SUPPLY |  | Mtr |  | 0
| LAYING & termination |  | Mtr |  | 0
13 | 4 Core x 6 Sqmm Cu Cable (XLPE) for distribution inside building from MDB to all sub- DBS / street lighting etc
| SUPPLY | 300 | Mtr |  | 0
| LAYING & termination | 300 | Mtr |  | 0
14 | 3 Core x 6 Sqmm Cable PVC - YFY.
| SUPPLY |  | Mtr |  | 0
| LAYING & termination |  | Mtr |  | 0
15 | 3 Core x 4 Sqmm Cable PVC - YFY.
| SUPPLY |  | Mtr |  | 0
| LAYING & termination |  | Mtr |  | 0
16 | 3.5 Core x 2.5 Sqmm Cu Cable (XLPE) for distribution inside building from MDB to all sub- DBS / street lighting etc
| SUPPLY | 500 | Mtr |  | 0
| LAYING by undergorund at 0.75 M depth covered by brick layer with provision of route marker or by cable tray/ GI pipe laying | 500 | Mtr |  | 0
C 3 | CIVIL WORKS FOR OUTDOOR CABLE LAYING :
C3.1 | Preparation of outdoor cable trenches including excavation & back filling with sand & cable tiles compaction, route marker at every 20 M as per specification of the following sizes.
1 | Trench of width 200mm & depth 750mm | 300 | Mtr |  | 0
2 | Trench of width 300mm & depth 750mm | 750 | Mtr |  | 0
C | TOTAL FOR POWER & CONTROL CABLES |  |  |  | 0
D | LOADBREAK SWITCHES/SOCKETS/
SWITCHFUSE UNITS/ STARTERS:
Supply, erection, testing and
commissioning of switchfuse unit/loadbreak switch, with factory made
16G sheet steel enclosure mounted on angle iron frame work/grouted into
walls, using necessary fixing accessories. The rate shall include for
necessary incoming/outgoing cable termination boxes in this item only. The
steel supports, grip bolts etc.,required for erection will be measured
separately under the heading "steel item/grip bolts".
INDUSTRIAL TYPE:WITH PLUG TOPS
Supply, erection, testing and commissioning of factory made metal clad
totally enclosed with cast aluminium housing with industrial
socket/interlocked combined rotary switch and socket with scrapping earth
connection and plug top. In case of interlocked socket, the interlocking
should ensure that the plug cannot be inserted or withdrawn while the switch
is in 'ON' position. (all switches & sockets shall be housed in painted MS
boxes). The erection rate shall include supply of angle iron frame work and
fixing accessories such as grip bolts/grouting/ welding to steel structures etc.
2 | 16 Amps, 3-pin (240V) 1 phase industrial
box,controlled by 16 Amps, SPN MCB.
| SUPPLY | R.O. | Each |  | -
| ERECTION | R.O. | Each |  | -
D2 | DOMESTIC TYPE :
Supply, erection, testing and
commissioning of power points by
providing following switches/sockets
mounted on suitable size MS boxes fixed
flush/surface on to the wall with all
fixing and wiring accessories. Or workstation cubible - type switch boxes
1 | 6/16 Amps, 6-pin (250 Volts) single
phase universal socket with 16 A Switch.
single pole switch with
indicating lamp. The pin configuration
shall be round type. These sockets will
be used for normal power. Plug tops are
excluded from the scope of supply.
| SUPPLY | 80 | Each |  | 0
| ERECTION | 80 | Each |  | 0
2 | 20 Amps, 3-pin (240V) 1 phase universal shuttered socket with plug top located near the AC unit and controlled by 20 Amps DP switch with LED indicator,light switches.
| SUPPLY | 25 | Set |  | 0
| ERECTION | 25 | Set |  | 0
3 | Bank of 3Nos.6/16Amps, 3-pin (250 Volts) single phase commercial type socket controlled by 20 Amps SP Switch alongwith indicating lamp. The pin configuration shall be round type.These sockets will be used for UPS power.
| SUPPLY | 99 | Each |  | 0
| ERECTION | 99 | Each |  | 0
D | TOTAL FOR SWITCHES/SOCKETS/SWITCHFUSE UNITS |  |  |  | 0
E | SUBMAINS/CIRCUIT MAINS/POWER WIRING :
Supply and running of 1100 V grade PVC
insulated copper FRLS wires in 16 G
MS conduits as per specification titled
"DISTRIBUTION SYSTEM, CONDUITS, WIRING
AND ACCESSORIES" and following details.
The rate shall include supply and
installation of all materials like
conduits, wires, fixing accessories,
etc. as detailed in Clause of above
mentioned specification.
1 | Supply and laying of 5 Runs of single core 16 Sq.mm and 2 Run of single core 6 Sqmm PVC insulated multistrand copper conductors in 1 No. of 32mm dia PVC conduits with all necessary accessories complete as required.-- FROM 20KVA UPS TO UPS O/P PANEL
| SUPPLY | 120 | Mtrs |  | 0
| LAYING | 120 | Mtrs |  | 0
2 | Supply and laying of 4 Runs of single core 10Sq.mm and 2 Run of single core 6Sqmm PVC insulated multistrand copper conductors in 1 No. of 32mm dia PVC conduits with all necessary accessories complete as required.
| SUPPLY | 450 | Mtrs |  | 0
| LAYING | 450 | Mtrs |  | 0
3 | Supply and laying of 4 Runs of single core 6Sq.mm and 2 Run of single core 4Sqmm PVC insulated multistrand copper conductors in 1 No. of 32mm dia PVC conduits with all necessary accessories complete as required.
| SUPPLY | 300 | Mtrs |  | 0
| LAYING | 300 | Mtrs |  | 0
4 | Supply and laying of 2 Runs of single core 4Sq.mm and 1 Run of single core 2.5Sqmm PVC insulated multistrand copper conductors in 1 No. of 25mm dia PVC conduits with all necessary accessories complete as required.
| SUPPLY | 2200 | Mtrs |  | 0
| LAYING | 2200 | Mtrs |  | 0
E | TOTAL FOR SUBMAINS/CIRCUIT MAINS/POWER WIRING |  |  |  | 0
F | EARTHING SYSTEMS
F1 | EARTHING STATIONS:
Providing the earth stations with
necessary materials, labour, civil
works, etc. as per Indian Standard
specification IS:3043 etc. complete.
1 | 3 mtrs long 50 mm dia. G.I pipe
electrode earth station.The chamber size
shall be 450 x 450 mm with C.I. Cover
plate. The identification number shall
be provided both inside and outside.
| SUPPLY | 4 | Each |  | 0
| ERECTION | 4 | Each |  | 0
2 | 600 x 600 x 3.15 mm copper plate
electrode earth station.The chamber
size shall be 450 x 450 mm with C.I.
Cover plate. The identification number shall be
provided both inside and outside of equipment.
| SUPPLY | 6 | Each |  | 0
| ERECTION | 6 | Each |  | 0
F2 | EARTHING TAPES/WIRES:
Supply and running of earth tapes / wires as per specification, complete. Erection rate shall be for both indoor and outdoor inclusive of earth excavation work.
1 | 50 x 6 mm GI tape (Hot dip galvanised)
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
2 | 40 x 6 mm GI tape (Hot dip galvanised)
| SUPPLY | R.O. | Mtr
| ERECTION | R.O. | Mtr
3 | 25 x 6 mm GI Tape (Hot Dip Galvanized)
| SUPPLY | 150 | Mtrs |  | 0
| ERECTION | 150 | Mtrs |  | 0
4 | 25 x 3 mm GI tape (Hot dip galvanised)
| SUPPLY | 100 | Mtr |  | 0
| ERECTION | 100 | Mtr |  | 0
5 | Supply and laying of 2 Run of single core 16Sq.mm in existing PVC conduit with all necessary accessories complete as required. --UPS EARTHING
| SUPPLY | 200 | Mtrs |  | 0
| LAYING | 200 | Mtrs |  | 0
F | TOTAL FOR EARTHING SYSTEM |  |  |  | 0
G | MISCELLANEOUS ITEMS :
G1 | PIPES :
Supply and laying of pipes in wall/floor
/in ground including chipping/excavation
laying and making good the surface as
required. Any collars and bends and
nipples required shall be laid at a
depth of 900 mm below ground level or
under paved areas/under floor as required.
1 | 100 mm dia Class 'B' GI pipe.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
2 | 50mm dia PVC pipe 4mm thick with bends, collars etc.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
3 | 65mm dia GI pipe Class B with bends, collars etc.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
4 | 150 mm dia Hume pipe.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
5 | 300 mm dia Hume pipe.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
G2 | STEEL ITEMS, CABLE TRAYS :
Supply,fabrication,erection & epoxy painting of steel items as required as per specification complete, Generally steel items include cable tray, cable tray suppoting arrangements,MS Channels-(ISMC),Angles,Plates,Grip bolts,rod supports and any other steel items not covered in other items of schedule of quantities. The cable trays shall be as per specification titled "CABLE TRAYS" and shall be of ladder type made of angles and flats with suitable M.S Sheet cover whereall required.The rate shall also include painting with two coats of red oxide and primer and two coats of synthetic enamel paint of approved shade.
| SUPPLY | R.O. | M.T. |  | -
| ERECTION | R.O. | M.T. |  | -
G4 | PERFORATED TYPE CABLE TRAYS
Supply & erection of the following sizes
Perforated type cable tray made of Pre galvanized 2MM
sheet and finished with good quality paint
with necessary supports like plates,fasteners etc.
brackets,angle iron,suspension are measured
separately the heading "Steel Items".
3 | 600 x70x2 MM Pre Galavanized ladder Type Tray
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
Horizantal Bend
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
Vertical Bend
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
T-Joint
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
4 | 450 x70x2 MM Pre Galavanized ladder Type Tray
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
Horizantal Bend
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
Vertical Bend
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
T-Joint
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
5 | 300 x70x2 MM Pre Galavanized ladder Type Tray
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
Horizantal Bend
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
Vertical Bend
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
T-Joint
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
G5 | CASING-N-CAPPING:
1 | 15 mm width.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
2 | 25 mm width.
| SUPPLY | R.O. | Mtr |  | -
| ERECTION | R.O. | Mtr |  | -
G6 | PROVDING & FIXING THE FOLLOWING
MISCELLANEOUS ITEMS:
1 | 4 Fire buckets of 9 Lts capacity with
floor stand, painting, etc.
| SUPPLY & ERECTION | 1 | Each |  | 0
2 | Rubber mats of 1.1 KV grade 1.8 Mtrs x
| 0.9 Mtrs and of sufficient thickness in front of all panels | 3 | Each |  | 0
3 | Shock treatment chart with teak wood
| frame and glass cover as approved in all electrical rooms | 3 | Each |  | 0
4 | Electrical single line diagram (As Built
| drawing) with teak wood frame and glass cover. | 3 | Each |  | 0
5 | First Aid Box. | 3 | Set |  | 0
G | TOTAL FOR MISCELLANEOUS ITEMS |  |  |  | 0
A B S T R A C T
A | Switchboard DBs & Electrical equipments/ systems |  |  |  | 0
B | FACTORY BUILT MCB DISTRIBUTION BOARDS |  |  |  | 0
C | POWER AND CONTROL CABLES |  |  |  | 0
D | SWITCHES/SOCKETS/SWITCHFUSE UNITS/STARTERS |  |  |  | 0
E | SUBMAINS/CIRCUIT MAINS/POWER WIRING |  |  |  | 0
F | POWER EARTHING SYSTEM |  |  |  | 0
G | MISCELLANEOUS ITEMS |  |  |  | 0
H | Electrical Inspectorate clearance for panel installation shall also be in scope of party | 1 | Lot |  | 0
| GRAND TOTAL |  |  |  | 0

## Other Infra
Schedule-A8
Other Infrastructure around - Servcie Building
Sl. No. | Particulars | Unit | Qty | Rate | Amount
1 | Car Parking
1.01 | Excavation in all types of soil including dense soil, disintegrated/ weathered/ soft rock (Poclainable) for Footings of columns, Retaining walls, Core walls, catch pits, Lift pits, trenches for drains, etc., by mechanical means including manual excavation for leveling, dressing the edges, with all leads and lifts including back filling in layers of 150mm with watering and compaction. Dewatering of both ground and surface water, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, struting, required for keeping earth in position etc, Rate to include disposing the excess earth and spreading in layers to the required levels within the site wherever specified and carting away out side the site to the designated areas identified by the local authorities. Note:PCC area shall be considered for measurement (Working space & provision of slopes if required for execution shall not be paid separately). | Cum | 500 |  | 0
1.02 | Supply and filling in foundations and the area whereever specified with approved good quality filling materials in plinths, area development etc. wherever specified in layers of not exceeding 150 mm thick including breaking clods,storing,transportation ,double handling, watering, compacting each layer with vibratory compactor and at unaccessible places with wooden/steel rammers to achieve 90 to 95% proctor density at optimum moisture content, all leads and lifts, bailing/ pumping out of water to keep site dry while backfilling; cost shall include conveyance of all materials, labour, machinery etc. complete as directed.The rate to includes loading,unloading, hire and fuel charges for tools and plants and other incidental charges etc., complete.
a | With excavated earth available at site ( for Foundtion & Sides of Retaining walls) | Cum | 400 |  | 0
b | With approved quality earth brought from outside | Cum | NA
1.03 | Providing Laying, spreading and compacting stone aggregate of specified sizes to WBM (53 to 20) specifications in uniform thickness, hand picking, rolling with 3 wheeled road / vibratory roller 8-10 tonne capacity in 3 stages to proper grade and camber, applying and brooming requisite type of screening / binding material to fill up interstices of coarse aggregate, watering and compacting to the required density . It has to laid in first layer depth 100 mm and required layers depth 75 mm . | CuM | 75 |  | 0
1.04 | Providing and laying P.C.C. 1:4:8 of specified th. wherever specified using river sand, 40mm and down size metal including sub grade preparation,leveling, all leads and lifts,rough finishing at the top surface,curing and shuttering if necessary etc., | Cum | 37.5 |  | 0
1.05 | Providing, batching, mixing, transporting through transit mixers, pumping and laying Reinforced Cement Concrete of specified grade at all levels and heights specified below using ordinary Portland cement of grade 53 from approved manufacturer, river sand, 20mm and down size coarse aggregates, necessary admixtures approved by Consultants (Conplast SP 430SRV from Fosroc or equivalent), including all leads and lifts, pumping using line pump or boom placer, vibrating/ compaction, scaffolding wherever necessary, curing as directed, including cost of shuttering and centering etc.of Grade M30 Concrete including providing , laying T12 of Rebar @ single layer 200cc. | CuM | 75 |  | 0
1.06 | Supply, fabrication, erection, painting with 2 coat zinc rich primer & 2 coat epoxy paint of MS Steel structural jobs as per detailed engineering & directions of EIC (All ISA, ISMC, tubular, piping etc materials covered) for making car shed | MT | 5 |  | 0
1.07 | Supply, erection with all accessories, water sealing & clamps etc of colored high asthetic tensile fabric roof of standrad make as per EIC direction for car shed | SqM | 400 |  | 0
| Sub total for Car Parking |  |  |  | 0
2 | RCC Approach Road & RCC Drain (100X7M Wide)
2.01 | Excavation in all types of soil including dense soil, disintegrated/ weathered/ soft rock (Poclainable) for Footings of columns, Retaining walls, Core walls, catch pits, Lift pits, trenches for drains, etc., by mechanical means including manual excavation for leveling, dressing the edges, with all leads and lifts including back filling in layers of 150mm with watering and compaction. Dewatering of both ground and surface water, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, struting, required for keeping earth in position etc, Rate to include disposing the excess earth and spreading in layers to the required levels within the site wherever specified and carting away out side the site to the designated areas identified by the local authorities. Note:PCC area shall be considered for measurement (Working space & provision of slopes if required for execution shall not be paid separately). | Cum | 700 |  | 0
2.02 | Supply and filling in foundations and the area whereever specified with approved good quality filling materials in plinths, area development etc. wherever specified in layers of not exceeding 150 mm thick including breaking clods,storing,transportation ,double handling, watering, compacting each layer with vibratory compactor and at unaccessible places with wooden/steel rammers to achieve 90 to 95% proctor density at optimum moisture content, all leads and lifts, bailing/ pumping out of water to keep site dry while backfilling; cost shall include conveyance of all materials, labour, machinery etc. complete as directed.The rate to includes loading,unloading, hire and fuel charges for tools and plants and other incidental charges etc., complete.
a | With excavated earth available at site ( for Foundtion & Sides of Retaining walls) | Cum | 500 |  | 0
b | With approved quality earth brought from outside | Cum | NA
2.03 | Providing Laying, spreading and compacting stone aggregate of specified sizes to WBM (53 to 20) specifications in uniform thickness, hand picking, rolling with 3 wheeled road / vibratory roller 8-10 tonne capacity in 3 stages to proper grade and camber, applying and brooming requisite type of screening / binding material to fill up interstices of coarse aggregate, watering and compacting to the required density . It has to laid in first layer depth 100 mm and required layers depth 75 mm . | CuM | 105 |  | 0
2.04 | Providing and laying P.C.C. 1:4:8 of specified th. wherever specified using river sand, 40mm and down size metal including sub grade preparation,leveling, all leads and lifts,rough finishing at the top surface,curing and shuttering if necessary etc., | Cum | 52.5 |  | 0
2.05 | Providing, batching, mixing, transporting through transit mixers, pumping and laying Reinforced Cement Concrete of specified grade at all levels and heights specified below using ordinary Portland cement of grade 53 from approved manufacturer, river sand, 20mm and down size coarse aggregates, necessary admixtures approved by Consultants (Conplast SP 430SRV from Fosroc or equivalent), including all leads and lifts, pumping using line pump or boom placer, vibrating/ compaction, scaffolding wherever necessary, curing as directed, including cost of shuttering and centering etc.of Grade M30 Concrete including providing , laying T12 of Rebar @ single layer 200cc. | CuM | 105 |  | 0
2.06 | Supply and Laying of Fly ash Paver Blocks(interlock type) of 80 mm thickness & M30 grade blocks with all complete as per specification, laid over 50 mm pcc and 25 mm mortar mix as approved inclusive of excavation , backfilling of 200 mm depth and compaction up to 95 % MDD. and as directed by engineer incharge .The block joints are filled using suitable fine material of cement & sand | Sqm | 240 |  | 0
2.07 | Supply and fixing of Hand rail 25mm MS pipe of 4 strands of span 2 m ,fixed on 2000 mm high poles of 40 mm MS Pipe grouted with M20 concrete(300mmx300mm) beneath ground 500 mm deep inclusive of fabrication and erection and tools and tackles for completion , all complete with two coats of primer & two coats of paint(overall DFT- 120 Micron) of approved make and colour all complete as per specification and direction of engineer incharge. Exposed height of handrail above gorund shall be of 1.5M and cross bracing to be provided in between 25 mm horizintal pipe in order to restrict trespassing | RM | 200 |  | 0
2.08 | Providing , fabrication and fixing of MS Grating (38mm x38 mm mesh size) , thickness 25 mm and unit weight of minimum 13 kg per sqm of approved make and with all complete as per specification and direction of EIC. Detailed drawing shall be submitted by contractor along with sample models for selection & approval by TSPL EIC | Sqm | 160
| Sub total for RCC Approach Road, Drain & Paver block path |  |  |  | 0
3 | Providing & Developing Front Lawn & Landscaping with all soil filling, plantation of hedge, lawn grass, decorative type Palm trees etc; Growing &maintaiining for 3 months with manuring & watering & then handing over to TSPL at good condition etc | SqM | 150 |  | 0
4 | Providing & devloping Sewage Treatment plant of Reed Bed natural system capable for handling Service building sewage water treatment of 120 personnel with all civil jobs- MBABR RCC tanks, sewage & clear water pumps, CPVC/ UPVC pipelines & fitting , HDPE lining, agrgates, brick bats , plantation of Reed bed & maintaining for 4 months & handing over to TSPL with demonstration of discharge water as per CPCB limits | Lumpsum | 1 |  | 0
| Total Cost |  |  |  | 0